## Net Analysis
Gross Energy Generation (GWh) | 254.8
Gross Capacity Factor | 48.8%
Loss Factors
Availability
Turbine Availability | 96%
Balance of Plant Availability | 99.7%
Grid Availability | 99.5%
Environmental Curtailment
Sector Management | 100%
High Wind Hysteresis | 99.8%
Icing Shutdown | 99%
Extreme Temperature | 99.7%
Wakes
Total Wakes | 97.1%
Electrical Efficiency
Total Electrical Efficiency | 97.5%
Consumptive Power | 100%
Turbine Efficiency
Turbine Performance | 98%
Turbulence Intensity | 98.4%
Inflow Angle | 100%
Environmental
Blade Soiling | 98.5%
Blade Degradation | 99.5%
Soft Icing | 99.5%
Aggregate Loss Factor | 83.6%
Net Energy Generation (GWh) | 212.9
Net Capacity Factor | 40.8%
Met Tower Uncertainty (% of P50 Wind Speed) | M2250 | M2315 | M2316 | M2317 | M2318 | M2322
Measurement | 2.5% | 2.1% | 2.2% | 3.2% | 3.4% | 3.1%
Vertical Extrapolation | 2.1% | 2% | 2% | 2% | 1.9% | 2%
MOS Correction | 0.7% | 1.8% | 2.3% | 2.6% | 2.3% | 3.1%
Climatic Variability | 1.4% | 1.3% | 1.3% | 1.4% | 1.3% | 1.3%
Combined Uncertainty | 3.7% | 3.6% | 4% | 4.8% | 4.7% | 4.9%
Project Uncertainty (% of P50 Energy) | 1-year | 5-year | 10-year | 20-year
Measurement | 2.5% | 2.5% | 2.5% | 2.5%
Vertical Extrapolation | 2.3% | 2.3% | 2.3% | 2.3%
MOS Correction | 2.4% | 2.4% | 2.4% | 2.4%
Climate Variability | 3.7% | 2.1% | 1.8% | 1.6%
Spatial Modeling | 1.5% | 1.5% | 1.5% | 1.5%
Power Modeling | 4.4% | 4.4% | 4.4% | 4.4%
Total Uncertainty | 7.3% | 6.6% | 6.5% | 6.5%
P-level (Capacity Factor) | 1-year | 5-year | 10-year | 20-year
Gross-P50 | 48.8% | 48.8% | 48.8% | 48.8%
Net-P50 | 40.8% | 40.8% | 40.8% | 40.8%
Net-P75 | 38.8% | 38.9% | 39% | 39%
Net-P90 | 37% | 37.3% | 37.4% | 37.4%
Net-P95 | 35.9% | 36.3% | 36.4% | 36.4%
Net-P99 | 33.9% | 34.5% | 34.6% | 34.6%
P-level (GWh/year) | 1-year | 5-year | 10-year | 20-year
Gross-P50 | 254.8 | 254.8 | 254.8 | 254.8
Net-P50 | 212.9 | 212.9 | 212.9 | 212.9
Net-P75 | 202.5 | 203.4 | 203.6 | 203.6
Net-P90 | 193.1 | 194.9 | 195.1 | 195.3
Net-P95 | 187.5 | 189.8 | 190.1 | 190.3
Net-P99 | 176.9 | 180.2 | 180.6 | 180.9
Net Analysis
version 1-1
CLIENT: BLACK HILLS CORP.
PROJECT: LACUMBRE
TURBINE: GE 2.5-127 AND GE 2.3-116
HUB HEIGHT: 89M and 80M
ALL DATA PRESENTED IN THIS PRELIMINARY REPORT ARE DRAFT AND ARE SUBJECT TO CHANGE DURING THE FINAL QUALITY CONTROL PROCESS.

## Turbine Means MWh
Turbine ID | Latitude | Longitude | Wind Speed | Density | Gross Generation | Wake Loss | Net Generation
|  |  | m/s | kg/m3 | MWh | % | MWh
T01 | 37.6022 | -104.5264 | 8.62 | 0.97711 | 11633 | 97.39% | 9748 | 11329
T02 | 37.5991 | -104.5251 | 8.67 | 0.97744 | 11703 | 96.58% | 9726 | 11302
T03 | 37.596 | -104.5259 | 8.44 | 0.9792 | 11381 | 97.2% | 9522 | 11062
T04 | 37.5921 | -104.5382 | 8.07 | 0.97969 | 10829 | 97.47% | 9074 | 10555
T05 | 37.5891 | -104.5348 | 8.03 | 0.98043 | 10780 | 96.43% | 8941 | 10395
T06 | 37.5859 | -104.5339 | 8.03 | 0.98066 | 10782 | 96.24% | 8926 | 10376
T07 | 37.5828 | -104.533 | 7.95 | 0.98162 | 10658 | 97.24% | 8918 | 10364
T08 | 37.5733 | -104.5674 | 7.84 | 0.97688 | 10426 | 98.46% | 8808 | 10266
T09 | 37.5679 | -104.5653 | 7.87 | 0.97656 | 10472 | 98.53% | 8848 | 10318
T10 | 37.5639 | -104.5557 | 8.05 | 0.9765 | 10794 | 97.5% | 9014 | 10524
T11 | 37.561 | -104.5508 | 8.08 | 0.97702 | 10842 | 96.94% | 9009 | 10510
T12 | 37.5582 | -104.5471 | 8.04 | 0.97737 | 10770 | 96.52% | 8926 | 10395
T13 | 37.5553 | -104.5453 | 7.95 | 0.97788 | 10593 | 97.21% | 8852 | 10298
T14 | 37.5523 | -104.5391 | 7.75 | 0.97952 | 8914 | 96.69% | 7350 | 8619
T15 | 37.5494 | -104.5356 | 7.9 | 0.97822 | 10492 | 97.74% | 8823 | 10255
T16 | 37.5453 | -104.5297 | 7.82 | 0.97758 | 10357 | 98.24% | 8761 | 10175
T17 | 37.5371 | -104.5098 | 7.87 | 0.97697 | 10372 | 97.67% | 8759 | 10130
T18 | 37.534 | -104.5074 | 7.81 | 0.97724 | 10259 | 97.65% | 8662 | 10018
T19 | 37.5534 | -104.5015 | 8.08 | 0.97716 | 10748 | 96.87% | 8993 | 10411
T20 | 37.5564 | -104.4981 | 8.12 | 0.97685 | 10829 | 96.39% | 9013 | 10438
T21 | 37.5553 | -104.4844 | 8.08 | 0.97665 | 10732 | 96.1% | 8928 | 10314
T22 | 37.5582 | -104.4813 | 8.24 | 0.97692 | 10994 | 96.35% | 9165 | 10593
T23 | 37.5493 | -104.4788 | 7.72 | 0.97916 | 8793 | 95.95% | 7234 | 8437
T24 | 37.5462 | -104.4739 | 8.06 | 0.97775 | 10694 | 96.5% | 8924 | 10321
|  | Total | 8.05 | 0.97802 | 254847 | 97.08% | 212924
Turbine Means MWh
version 1-1
CLIENT: BLACK HILLS CORP.
PROJECT: LACUMBRE
TURBINE: GE 2.5-127 AND GE 2.3-116
HUB HEIGHT: 89M and 80M
ALL DATA PRESENTED IN THIS PRELIMINARY REPORT ARE DRAFT AND ARE SUBJECT TO CHANGE DURING THE FINAL QUALITY CONTROL PROCESS.

## Turbine Means CF
Turbine ID | Latitude | Longitude | Wind Speed | Density | Gross Generation | Wake Loss | Net Generation
|  |  | m/s | kg/m3 | % | % | %
T01 | 37.6022 | -104.5264 | 8.62 | 0.97711 | 53.1% | 97.39% | 44.5% | 51.7%
T02 | 37.5991 | -104.5251 | 8.67 | 0.97744 | 53.4% | 96.58% | 44.4% | 51.57%
T03 | 37.596 | -104.5259 | 8.44 | 0.9792 | 51.9% | 97.2% | 43.5% | 50.48%
T04 | 37.5921 | -104.5382 | 8.07 | 0.97969 | 49.4% | 97.47% | 41.4% | 48.17%
T05 | 37.5891 | -104.5348 | 8.03 | 0.98043 | 49.2% | 96.43% | 40.8% | 47.44%
T06 | 37.5859 | -104.5339 | 8.03 | 0.98066 | 49.2% | 96.24% | 40.7% | 47.35%
T07 | 37.5828 | -104.533 | 7.95 | 0.98162 | 48.6% | 97.24% | 40.7% | 47.29%
T08 | 37.5733 | -104.5674 | 7.84 | 0.97688 | 47.6% | 98.46% | 40.2% | 46.84%
T09 | 37.5679 | -104.5653 | 7.87 | 0.97656 | 47.8% | 98.53% | 40.4% | 47.08%
T10 | 37.5639 | -104.5557 | 8.05 | 0.9765 | 49.3% | 97.5% | 41.1% | 48.02%
T11 | 37.561 | -104.5508 | 8.08 | 0.97702 | 49.5% | 96.94% | 41.1% | 47.96%
T12 | 37.5582 | -104.5471 | 8.04 | 0.97737 | 49.1% | 96.52% | 40.7% | 47.43%
T13 | 37.5553 | -104.5453 | 7.95 | 0.97788 | 48.3% | 97.21% | 40.4% | 46.99%
T14 | 37.5523 | -104.5391 | 7.75 | 0.97952 | 44.2% | 96.69% | 36.5% | 42.75%
T15 | 37.5494 | -104.5356 | 7.9 | 0.97822 | 47.9% | 97.74% | 40.3% | 46.79%
T16 | 37.5453 | -104.5297 | 7.82 | 0.97758 | 47.3% | 98.24% | 40% | 46.43%
T17 | 37.5371 | -104.5098 | 7.87 | 0.97697 | 47.3% | 97.67% | 40% | 46.22%
T18 | 37.534 | -104.5074 | 7.81 | 0.97724 | 46.8% | 97.65% | 39.5% | 45.71%
T19 | 37.5534 | -104.5015 | 8.08 | 0.97716 | 49% | 96.87% | 41% | 47.51%
T20 | 37.5564 | -104.4981 | 8.12 | 0.97685 | 49.4% | 96.39% | 41.1% | 47.63%
T21 | 37.5553 | -104.4844 | 8.08 | 0.97665 | 49% | 96.1% | 40.7% | 47.06%
T22 | 37.5582 | -104.4813 | 8.24 | 0.97692 | 50.2% | 96.35% | 41.8% | 48.34%
T23 | 37.5493 | -104.4788 | 7.72 | 0.97916 | 43.6% | 95.95% | 35.9% | 41.85%
T24 | 37.5462 | -104.4739 | 8.06 | 0.97775 | 48.8% | 96.5% | 40.7% | 47.09%
|  | Average | 8.05 | 0.97802 | 48.8% | 97.1% | 40.8%
Turbine Means CF
version 1-1
CLIENT: BLACK HILLS CORP.
PROJECT: LACUMBRE
TURBINE: GE 2.5-127 AND GE 2.3-116
HUB HEIGHT: 89M and 80M
ALL DATA PRESENTED IN THIS PRELIMINARY REPORT ARE DRAFT AND ARE SUBJECT TO CHANGE DURING THE FINAL QUALITY CONTROL PROCESS.

## Specifications
Project Specifications
Turbine Type(s): | GE 2.5-127 and GE 2.3-116
Hub Height: | 89m and 80m
Turbine Capacity: | 2500 kW and 2300kW
Number of Turbines: | 24
Number of External Turbines: | 50
Number of Future Turbines: | 0
Model Specifications
Reanalysis Dataset: | MERRA2
Number of Years: | 37
WRF Resolution (Temporal Dataset): | 4500m
WRF Resolution (Spatial Dataset): | 500m
TVM Resolution: | 90m
Observational Data
Meteorological Tower(s): | M2250 | M2315 | M2316 | M2317 | M2318 | M2322 | khokade
Top Sensor Height: | 59m | 60m | 60m | 60m | 61m | 60m | 80m
Time Series Start: | 2009-03-03 15:10 | 2010-05-27 17:10 | 2010-05-30 17:10 | 2010-06-10 17:20 | 2010-06-08 11:30 | 2010-06-12 17:10 | 2012-04-01
Time Series End: | 2012-01-31 07:50 | 2012-01-26 16:00 | 2011-07-28 13:40 | 2011-08-02 15:20 | 2011-10-24 10:20 | 2011-06-12 17:00 | 2013-04-01 11:30
Post QC Recovery Rate: | 82.85% | 79.37% | 89.35% | 78.33% | 92.22% | 93.96% | 91.83%
Loss Calculations
Turbine Availability: | Based on Vaisala's experience over the lifetime of a turbine.
Balance of Plant Availability: | This is based on 24 hours of outage time per year.
Grid Availability: | Based on grid availability forecast for the region.
Sector Management: | Standard minimum turbine spacing of five rotor diameters parallel to the dominant wind direction is
tested against the layout.
High Wind Hysteresis: | Based on the percentage of time when the wind speed is below the cut-out and above the re-cut-in wind speed
after a high wind cut-out event.
Icing Shutdown | Based on the percentage of time the turbine blade are expected to be affected by ice build-up.
Extreme Temperature: | Based on the percentage of time when ambient temperature is expected to be above the operating temperature.
Wakes: | Wake loss calculated using Vaisala's proprietary time varying wake model.
Collection System Efficiency: | This value covers the efficiency of all components from the turbines to the substation
Substation Transformer Efficiency: | Vaisala assumes that the plant will be metered on the low voltage side of the substation transformer
HV Transmission Line Efficiency: | Vaisala assumes that the plant will be metered on the low voltage side of the substation transformer
Turbine Performance: | Based on Vaisala’s experience with wind farms in the region, turbines do not perform exactly at the manufacturer's
stated power curve.
Turbulence Intensity: | Turbine inefficiency resulting from the statistical averaging of the power curve and periods of high stability.
Inflow Angle: | Based on the slope of the terrain leading up to the wind turbine.
Blade Soiling: | Turbine inefficiency due to a build up of material on the turbine blades.
Soft Icing: | Turbine inefficiency due to ice build up on blades.
Blade Degradation: | Turbine inefficiency due to damage to the turbine blades cause by debris in the air.
Uncertainty Calculations
Measurement: | Measurement uncertainty covers quality of anemometers, availability of data, tower configuration, boom lengths
and whether towers have been visited in a site visit. It also covers the statistical propagation of these errors
through the shear calculation.
Vertical Extrapolation: | Vertical extrapolation is the process of using tower height wind speeds to estimate hub height wind speeds.
This uncertainty is based on the difference between measurement heights and hub height.
MOS Correction: | MOS correlation uncertainty is based on the length of observational record and the fit of the simulated time series
to the observational data.
Climate Variability: | Climate variability is comprised of three components. The probability that the period Vaisala used as the historic
climate represents the true climate. The probability that the climate of the future prediction period will capture
the true climate and the probability that the climate is changing.
Spatial Modeling: | Spatial modeling captures the effects of mesoscale models calibrated to the met tower locations and its ability to
predict turbine locations. It is comprised of two components, a mesoscale and microscale uncertainty that are
a function of the models that Vaisala uses. This complex uncertainty considers the spatial covariance between
every turbine and met tower location.
Power Modeling: | Power modeling uncertainty is based on the conversion from Gross P50 wind speed to Net P50 energy.
Specifications
version 1-1
CLIENT: BLACK HILLS CORP.
PROJECT: LACUMBRE
TURBINE: GE 2.5-127 AND GE 2.3-116
HUB HEIGHT: 89M and 80M
ALL DATA PRESENTED IN THIS PRELIMINARY REPORT ARE DRAFT AND ARE SUBJECT TO CHANGE DURING THE FINAL QUALITY CONTROL PROCESS.

## 8760-avg
Date are in local time (UTC -7)
Values represent the average value for each hour of the year based on the 37-year timeseries
This if NOT a "typical" year
MWh | HOUR
DAY | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
1 | 33.9743 | 35.1149 | 34.048 | 32.518 | 32.84 | 32.2181 | 31.1706 | 29.917 | 29.8282 | 29.6539 | 26.3548 | 22.9226 | 22.554 | 22.2958 | 21.379 | 22.3133 | 22.0075 | 24.5321 | 23.832 | 20.246 | 19.6066 | 20.4343 | 23.9219 | 26.1069
2 | 28.3558 | 30.0118 | 30.8962 | 31.543 | 32.2271 | 33.4345 | 32.9406 | 32.2303 | 32.2197 | 31.4831 | 28.5741 | 25.5075 | 23.2572 | 20.6723 | 16.6515 | 15.4061 | 15.6791 | 18.1401 | 23.5113 | 26.9386 | 28.6672 | 30.7382 | 31.9557 | 31.8922
3 | 33.0566 | 32.3591 | 31.3509 | 33.8806 | 33.7118 | 33.4935 | 33.8688 | 34.4791 | 33.7345 | 32.2452 | 29.2102 | 26.9334 | 26.8637 | 26.5806 | 26.541 | 26.5698 | 27.3052 | 30.5417 | 31.3423 | 27.6008 | 27.018 | 26.6975 | 28.6489 | 29.0081
4 | 28.9713 | 29.4474 | 30.5888 | 30.1435 | 30.6092 | 31.5524 | 28.9011 | 29.3767 | 29.8809 | 28.4158 | 25.3814 | 23.133 | 23.35 | 23.8323 | 22.7636 | 21.8974 | 22.567 | 26.9954 | 29.8927 | 28.9849 | 30.665 | 28.6599 | 30.0913 | 30.9551
5 | 31.7198 | 31.6268 | 32.1441 | 31.0487 | 33.5801 | 35.076 | 35.9525 | 33.9083 | 33.8561 | 32.5896 | 28.3763 | 27.0726 | 26.9295 | 24.985 | 25.7515 | 27.3184 | 30.7101 | 35.5013 | 35.3814 | 35.0289 | 31.9694 | 30.0715 | 30.0709 | 30.307
6 | 31.3903 | 32.1909 | 30.0401 | 28.5489 | 30.179 | 30.5975 | 31.0033 | 31.2303 | 31.0101 | 28.6191 | 24.1747 | 19.9134 | 18.2457 | 16.5296 | 15.0613 | 16.8143 | 19.255 | 20.9409 | 21.5732 | 21.3881 | 20.8893 | 21.2525 | 24.4701 | 27.3954
7 | 30.6072 | 31.8544 | 32.2991 | 34.3997 | 36.8614 | 36.6617 | 34.5905 | 34.1314 | 34.4841 | 31.8929 | 25.0043 | 19.0121 | 18.4891 | 17.8665 | 17.6448 | 21.7917 | 23.5757 | 25.9046 | 26.4751 | 27.6503 | 25.299 | 24.3901 | 27.9613 | 32.2645
8 | 33.9579 | 33.8266 | 35.1747 | 37.9229 | 36.8481 | 34.8365 | 32.8515 | 33.984 | 34.8808 | 34.3913 | 29.8972 | 26.5662 | 24.2909 | 22.2094 | 22.123 | 24.3341 | 27.8119 | 30.3198 | 30.0878 | 28.5246 | 29.586 | 30.9375 | 30.5177 | 31.315
9 | 32.9794 | 34.8181 | 34.8132 | 33.2716 | 31.9847 | 31.7298 | 31.8286 | 32.4497 | 31.9103 | 31.3589 | 29.532 | 26.3714 | 24.2491 | 22.2585 | 20.5063 | 20.8239 | 20.983 | 24.5045 | 26.6104 | 22.0908 | 19.907 | 20.6754 | 22.0062 | 24.086
10 | 28.6922 | 32.0623 | 32.3974 | 34.0262 | 34.3601 | 34.0473 | 34.0283 | 34.1957 | 35.3417 | 37.086 | 33.7012 | 27.9265 | 25.4367 | 24.7549 | 25.2114 | 26.2794 | 28.1811 | 29.7526 | 30.7178 | 30.0306 | 27.3849 | 29.7029 | 32.6734 | 34.9121
11 | 35.9757 | 36.1579 | 37.634 | 41.5259 | 42.6404 | 41.0107 | 40.0824 | 38.3834 | 36.6841 | 33.5638 | 31.8698 | 30.0866 | 27.8178 | 25.6163 | 23.8575 | 25.1528 | 25.4068 | 28.0559 | 30.8643 | 31.5118 | 26.8697 | 24.1766 | 25.9809 | 28.6579
12 | 32.4865 | 34.0224 | 33.543 | 34.7634 | 36.8439 | 37.2006 | 36.844 | 34.8447 | 34.0643 | 31.776 | 26.2718 | 20.5066 | 18.5406 | 19.2835 | 18.2683 | 21.3111 | 23.3725 | 24.6612 | 24.9815 | 22.4842 | 21.8036 | 22.3678 | 24.4415 | 26.5786
13 | 29.9176 | 33.3172 | 35.3662 | 37.2842 | 38.5785 | 38.4878 | 35.9137 | 33.9319 | 33.0443 | 31.7509 | 26.1405 | 20.9649 | 19.5198 | 18.8826 | 19.2198 | 21.6187 | 23.9731 | 26.72 | 30.7485 | 29.8976 | 29.8579 | 29.211 | 30.552 | 32.0762
14 | 33.665 | 34.3441 | 33.6777 | 33.1045 | 32.634 | 31.9223 | 31.537 | 30.5457 | 30.1146 | 28.3753 | 26.2446 | 26.3166 | 25.452 | 23.2469 | 20.4964 | 21.618 | 21.7634 | 26.2958 | 26.2611 | 26.4276 | 25.8577 | 25.7103 | 28.1383 | 30.6467
15 | 32.4978 | 32.6982 | 32.4475 | 32.274 | 31.9174 | 33.0019 | 30.8622 | 30.2923 | 31.9159 | 31.6237 | 28.5163 | 26.265 | 25.7111 | 26.8528 | 27.33 | 29.2263 | 30.0728 | 31.8118 | 33.3662 | 30.5137 | 28.4146 | 29.1007 | 32.243 | 33.8831
16 | 35.8218 | 37.7159 | 36.4526 | 32.3868 | 34.7317 | 36.393 | 33.8932 | 33.3427 | 31.9453 | 30.2548 | 27.0966 | 22.5466 | 21.8205 | 20.9957 | 20.0352 | 22.3736 | 23.1298 | 28.9007 | 30.1875 | 26.9111 | 24.2994 | 24.7471 | 27.4491 | 29.1342
17 | 30.9174 | 31.3326 | 31.4837 | 31.7853 | 31.573 | 31.1587 | 32.1303 | 32.7856 | 33.198 | 30.9833 | 27.1235 | 25.3762 | 23.3121 | 23.8843 | 22.7056 | 23.194 | 23.5662 | 25.8082 | 26.0867 | 25.8788 | 25.4242 | 26.4542 | 29.1506 | 31.7818
18 | 35.615 | 36.0185 | 35.6967 | 35.4863 | 34.4112 | 32.701 | 32.4975 | 32.4994 | 33.6087 | 33.3017 | 25.0561 | 20.3405 | 17.4134 | 17.483 | 18.6613 | 20.5936 | 21.8831 | 28.3053 | 30.9389 | 31.6614 | 29.6088 | 29.2464 | 29.7375 | 34.0161
19 | 37.171 | 38.0883 | 39.6135 | 41.4123 | 40.8458 | 39.3575 | 39.6803 | 39.0588 | 38.1731 | 36.1975 | 33.304 | 29.8072 | 26.0955 | 24.6123 | 23.4717 | 23.4369 | 24.25 | 26.1002 | 26.0767 | 23.1444 | 23.0983 | 26.372 | 30.3628 | 31.8124
20 | 33.0789 | 32.4657 | 31.8618 | 32.1793 | 29.7743 | 28.5606 | 27.8625 | 27.7995 | 27.006 | 27.1121 | 26.3542 | 23.0843 | 23.5105 | 24.5577 | 24.4751 | 27.4859 | 28.263 | 30.5085 | 28.598 | 27.7145 | 26.1238 | 26.2988 | 28.5021 | 30.4173
21 | 32.715 | 33.8572 | 34.6272 | 34.422 | 36.6592 | 37.5982 | 36.3459 | 33.4947 | 32.8828 | 31.3186 | 26.8943 | 26.2986 | 23.9091 | 22.4748 | 22.5494 | 25.8549 | 26.7279 | 29.243 | 30.1343 | 30.0583 | 27.6973 | 26.5421 | 27.7904 | 31.0143
22 | 33.933 | 34.9632 | 34.7036 | 35.3625 | 34.3846 | 31.5112 | 29.7659 | 28.8969 | 30.2004 | 30.8992 | 26.2987 | 24.0404 | 22.5922 | 21.6495 | 20.733 | 21.1424 | 23.0896 | 24.3475 | 23.6477 | 22.6548 | 25.8877 | 28.5757 | 31.4068 | 34.9902
23 | 37.1352 | 38.6965 | 39.9511 | 42.4032 | 42.7092 | 42.2048 | 41.143 | 39.9627 | 39.7531 | 39.0816 | 35.8268 | 31.0582 | 25.4009 | 23.321 | 23.4187 | 25.2898 | 25.2863 | 29.3803 | 29.8944 | 29.8988 | 27.4773 | 29.2448 | 35.117 | 35.3759
24 | 34.9681 | 35.8221 | 35.7826 | 37.7073 | 37.2177 | 37.3233 | 36.5651 | 37.019 | 36.5688 | 34.8757 | 29.5177 | 27.6657 | 27.1739 | 26.7623 | 27.5684 | 29.4143 | 27.3838 | 27.8996 | 25.6945 | 27.9553 | 29.6346 | 30.3641 | 32.1452 | 33.8191
25 | 34.7242 | 33.7627 | 35.5918 | 36.6204 | 35.0589 | 31.8719 | 30.2747 | 29.9203 | 31.6367 | 30.1283 | 24.6806 | 21.5644 | 22.8254 | 22.3926 | 23.3352 | 25.2721 | 26.6828 | 28.3558 | 30.484 | 30.6937 | 29.9855 | 27.1082 | 29.3179 | 32.7526
26 | 31.5746 | 30.7359 | 30.9957 | 30.7136 | 31.6653 | 31.9908 | 30.7652 | 30.4973 | 32.0902 | 32.7841 | 29.2843 | 24.8966 | 22.5554 | 21.1119 | 21.7692 | 22.3619 | 23.8371 | 25.7411 | 28.2887 | 28.8014 | 28.74 | 29.56 | 29.1676 | 31.3211
27 | 32.8949 | 32.7198 | 33.1248 | 33.178 | 35.0323 | 35.808 | 36.33 | 35.3479 | 35.6691 | 34.3734 | 31.0778 | 27.2553 | 25.9226 | 24.2009 | 24.5398 | 27.2019 | 27.1478 | 28.0217 | 29.3386 | 27.5141 | 24.3559 | 23.9357 | 26.1729 | 27.8056
28 | 28.7215 | 29.9932 | 32.4283 | 33.9893 | 34.639 | 34.0486 | 33.9921 | 33.9173 | 33.8828 | 35.1977 | 31.4883 | 29.9574 | 27.2722 | 25.1527 | 25.2418 | 25.833 | 26.1729 | 27.1441 | 30.9835 | 30.3162 | 28.8753 | 29.2977 | 30.6739 | 31.172
29 | 29.1786 | 28.5527 | 28.0102 | 29.1361 | 28.8768 | 28.9538 | 29.7088 | 31.4828 | 31.8295 | 31.9083 | 26.7988 | 23.532 | 21.4309 | 19.7396 | 20.9299 | 23.4687 | 24.3211 | 25.1135 | 26.1413 | 28.397 | 27.0057 | 27.5337 | 29.6856 | 30.2772
30 | 30.0948 | 30.7458 | 31.2267 | 32.2461 | 32.7531 | 32.4793 | 31.3678 | 32.0457 | 33.6722 | 32.735 | 27.9355 | 25.1946 | 24.1689 | 23.6806 | 22.3541 | 24.234 | 26.8724 | 27.8539 | 28.5267 | 27.838 | 26.1953 | 26.3545 | 30.2835 | 32.7742
31 | 32.5901 | 32.4894 | 31.8838 | 32.9597 | 32.1468 | 31.1016 | 29.9261 | 30.3146 | 29.5692 | 27.8492 | 22.5612 | 22.099 | 22.9366 | 21.4004 | 22.8082 | 25.1391 | 25.3482 | 28.0056 | 27.8827 | 27.526 | 22.6509 | 22.7648 | 24.5492 | 26.1071
32 | 26.8278 | 28.6884 | 30.6254 | 30.1878 | 30.6067 | 29.7603 | 29.587 | 29.1886 | 29.0597 | 28.9132 | 27.5651 | 25.9864 | 23.1345 | 21.1961 | 22.0384 | 26.2973 | 25.4663 | 21.3891 | 24.7193 | 25.9368 | 24.5096 | 23.693 | 28.4785 | 31.7692
33 | 33.5299 | 34.1029 | 36.3298 | 37.4179 | 36.5999 | 34.2631 | 33.4608 | 33.1975 | 32.3789 | 31.1516 | 27.7906 | 23.8308 | 21.0861 | 18.7159 | 16.9578 | 18.9169 | 22.2238 | 20.9808 | 21.2535 | 22.2202 | 23.6714 | 22.9641 | 23.5046 | 24.8228
34 | 26.3741 | 27.9117 | 28.5511 | 30.6627 | 32.5632 | 31.5913 | 31.5207 | 32.88 | 33.2489 | 31.9329 | 26.138 | 24.2628 | 22.2979 | 20.7221 | 21.4762 | 23.1584 | 24.3253 | 24.0011 | 23.8332 | 22.0062 | 19.7368 | 20.5059 | 22.1438 | 26.0313
35 | 26.2145 | 26.6561 | 28.1078 | 29.972 | 29.8142 | 27.077 | 27.7469 | 27.208 | 26.8766 | 29.4385 | 25.387 | 26.6219 | 25.465 | 21.2458 | 21.0981 | 26.2181 | 28.0193 | 27.3421 | 30.303 | 27.3319 | 24.959 | 24.4472 | 24.3673 | 25.8965
36 | 26.0017 | 27.2889 | 27.784 | 28.9178 | 28.8993 | 27.2002 | 26.979 | 26.331 | 26.8668 | 27.5932 | 26.7677 | 27.5408 | 27.9915 | 24.725 | 25.4393 | 26.7416 | 26.707 | 23.2326 | 25.7581 | 25.0817 | 21.8955 | 19.9255 | 20.7718 | 22.5938
37 | 23.3573 | 25.1037 | 29.7772 | 32.8007 | 36.6847 | 36.0258 | 36.1408 | 35.478 | 34.621 | 35.5368 | 31.2673 | 27.8709 | 24.1087 | 21.643 | 23.0781 | 26.1747 | 27.8285 | 26.918 | 27.0666 | 28.1364 | 30.6938 | 32.7037 | 33.0232 | 32.314
38 | 30.5664 | 30.5148 | 31.4794 | 31.8175 | 32.0322 | 31.8015 | 31.9324 | 31.3078 | 31.1978 | 28.291 | 22.4388 | 21.7075 | 22.0608 | 21.7979 | 22.0924 | 21.8294 | 21.6508 | 22.1368 | 24.0309 | 26.965 | 27.6608 | 26.8049 | 27.66 | 29.9675
39 | 29.3137 | 30.0077 | 30.5099 | 32.3425 | 31.0176 | 28.3144 | 27.2823 | 27.1828 | 27.3776 | 27.6983 | 26.9459 | 26.8088 | 26.3934 | 24.5269 | 24.7568 | 27.2192 | 27.6552 | 24.5898 | 25.1868 | 22.7882 | 21.6643 | 20.7926 | 23.4662 | 26.6758
40 | 26.1066 | 27.3528 | 29.5933 | 30.7889 | 32.9437 | 32.0913 | 31.6936 | 31.5642 | 32.799 | 33.4017 | 28.7837 | 26.4472 | 26.6637 | 24.8425 | 25.6418 | 27.077 | 26.4766 | 25.8487 | 28.7608 | 29.5136 | 28.4861 | 27.942 | 30.2684 | 32.7144
41 | 31.446 | 31.3628 | 32.3054 | 33.9175 | 33.7491 | 32.3506 | 32.7862 | 32.8983 | 32.8132 | 32.0688 | 28.7305 | 28.2378 | 24.7899 | 23.7327 | 23.9364 | 26.2757 | 25.7795 | 25.2622 | 23.6448 | 21.1141 | 18.6114 | 18.0102 | 21.1244 | 25.2187
42 | 24.2814 | 25.4079 | 27.4945 | 27.6302 | 27.4685 | 26.7868 | 28.4282 | 29.4539 | 30.3401 | 29.8276 | 26.6053 | 25.5054 | 25.0089 | 23.5656 | 22.9439 | 24.3705 | 24.6654 | 21.7384 | 22.1665 | 22.6643 | 20.1334 | 16.721 | 18.6803 | 21.4327
43 | 22.7296 | 23.7887 | 26.5229 | 29.551 | 31.2401 | 31.2405 | 32.0948 | 32.4392 | 32.4357 | 29.4467 | 23.1265 | 22.6675 | 22.3534 | 19.2597 | 20.821 | 25.0671 | 25.4659 | 25.6228 | 28.2033 | 27.4796 | 23.9262 | 25.249 | 30.2668 | 33.7583
44 | 36.6773 | 35.9566 | 36.7993 | 39.0082 | 41.3357 | 41.6836 | 40.9788 | 40.4613 | 38.2344 | 35.003 | 31.1659 | 27.7649 | 25.7718 | 24.2578 | 25.9547 | 27.1331 | 26.6517 | 24.8671 | 27.3838 | 26.6224 | 25.2997 | 25.7172 | 29.1568 | 32.9009
45 | 31.8683 | 32.3073 | 36.0261 | 36.5795 | 36.3159 | 33.9275 | 34.2134 | 35.0037 | 33.6467 | 31.5766 | 27.2119 | 28.0712 | 30.0394 | 29.3954 | 30.7166 | 30.3768 | 28.7924 | 26.8576 | 27.0988 | 25.7565 | 26.8591 | 27.3923 | 27.9629 | 28.6305
46 | 28.117 | 26.6544 | 28.4911 | 28.6494 | 26.7427 | 25.752 | 27.2718 | 30.5344 | 29.7275 | 28.8427 | 25.237 | 28.4917 | 26.3666 | 21.7357 | 20.8676 | 24.2263 | 25.3018 | 20.024 | 21.695 | 21.9141 | 21.8157 | 21.8837 | 24.3418 | 27.684
47 | 27.3805 | 27.8844 | 28.7364 | 29.3241 | 30.5719 | 29.6519 | 29.6619 | 27.8644 | 28.4013 | 27.2063 | 22.0396 | 21.7078 | 22.1714 | 19.5231 | 21.8525 | 23.8281 | 24.4608 | 24.6582 | 26.5435 | 25.8516 | 26.4503 | 27.0193 | 28.7907 | 32.214
48 | 31.1849 | 30.8965 | 35.4016 | 35.5795 | 35.3533 | 33.9827 | 32.9592 | 33.8822 | 33.3687 | 32.0308 | 26.6913 | 22.8231 | 21.4411 | 19.7617 | 21.002 | 22.9187 | 24.2395 | 25.9432 | 29.9575 | 26.7191 | 25.1778 | 25.9437 | 28.0339 | 28.4251
49 | 27.8004 | 28.375 | 30.2085 | 30.3364 | 29.4137 | 30.5639 | 31.503 | 31.6711 | 30.3434 | 28.5543 | 24.7891 | 24.5805 | 23.2263 | 22.3805 | 24.4701 | 27.4283 | 29.3431 | 28.002 | 28.6732 | 25.1403 | 24.6754 | 24.9899 | 26.8072 | 28.6554
50 | 27.2163 | 28.4685 | 28.9892 | 28.7438 | 28.66 | 29.5409 | 31.7456 | 32.5377 | 31.1826 | 30.3891 | 26.1595 | 23.9453 | 25.7633 | 27.3417 | 29.8204 | 30.6755 | 31.9849 | 29.8531 | 31.69 | 31.9029 | 32.2689 | 31.4222 | 33.1541 | 34.501
51 | 33.5957 | 32.847 | 32.599 | 33.0545 | 32.7403 | 31.7546 | 30.6593 | 29.5777 | 30.182 | 28.8414 | 20.6769 | 19.7142 | 20.3774 | 22.8164 | 23.505 | 23.755 | 25.4693 | 27.1816 | 26.3662 | 28.7564 | 25.899 | 24.6972 | 25.9069 | 28.4064
52 | 29.6731 | 29.8315 | 30.5972 | 33.0995 | 31.559 | 30.1971 | 29.5756 | 29.362 | 28.5171 | 26.369 | 24.0688 | 25.8462 | 27.0859 | 27.4832 | 26.4622 | 27.5362 | 30.2478 | 23.0953 | 20.4257 | 20.3439 | 17.8768 | 20.0814 | 24.3187 | 29.3461
53 | 30.132 | 31.7933 | 34.6725 | 36.4831 | 37.6386 | 36.3763 | 35.9406 | 35.5113 | 35.2673 | 32.2582 | 27.1946 | 25.3656 | 25.704 | 26.444 | 27.8707 | 31.9169 | 30.1194 | 27.9021 | 28.5445 | 28.2633 | 28.2259 | 27.5731 | 29.7459 | 29.1581
54 | 30.1164 | 30.9881 | 34.5487 | 34.1068 | 34.3008 | 32.2414 | 32.3295 | 33.2763 | 32.9351 | 29.6415 | 26.2904 | 27.7648 | 28.325 | 25.5746 | 25.2573 | 26.0102 | 26.3432 | 24.5925 | 26.6242 | 28.912 | 22.5842 | 22.5574 | 26.0891 | 30.2156
55 | 28.5391 | 26.4794 | 28.0013 | 30.8422 | 32.4153 | 32.9908 | 33.1477 | 32.868 | 32.2411 | 29.2812 | 25.0662 | 27.6112 | 26.7642 | 27.1493 | 28.9253 | 28.993 | 29.0473 | 28.7146 | 31.3286 | 30.2177 | 29.6134 | 29.6688 | 30.0903 | 30.3113
56 | 29.2078 | 31.6097 | 34.142 | 34.6016 | 33.6356 | 33.3254 | 32.7936 | 30.5637 | 29.2175 | 26.6995 | 23.846 | 24.4228 | 24.352 | 21.838 | 24.3525 | 25.6968 | 26.5643 | 24.3168 | 23.7594 | 25.8299 | 24.6442 | 24.6939 | 25.7319 | 27.4653
57 | 30.3677 | 31.0261 | 32.5289 | 33.6494 | 32.1717 | 30.1065 | 29.4336 | 30.45 | 31.1818 | 29.648 | 23.5025 | 21.9013 | 21.554 | 21.7856 | 23.5919 | 23.9914 | 25.0448 | 23.4405 | 25.5766 | 27.4827 | 24.7937 | 22.6231 | 23.0394 | 24.7064
58 | 25.0765 | 27.265 | 29.6181 | 31.0874 | 31.8325 | 30.3208 | 28.7218 | 28.8386 | 29.187 | 26.5826 | 22.2035 | 24.0223 | 22.5694 | 22.5919 | 21.1351 | 25.2507 | 26.8579 | 24.9662 | 26.6725 | 28.0775 | 23.4531 | 23.2488 | 24.4125 | 24.5918
59 | 24.9858 | 25.2679 | 27.7754 | 29.3521 | 31.6026 | 30.0168 | 27.7057 | 26.6935 | 26.6673 | 24.0884 | 20.1512 | 20.988 | 20.1079 | 19.973 | 21.5086 | 24.2072 | 25.5825 | 26.3586 | 24.8193 | 24.3462 | 23.7227 | 20.2221 | 21.715 | 22.5704
60 | 25.941 | 25.6279 | 26.9885 | 28.5044 | 30.2113 | 30.4145 | 32.2276 | 33.0178 | 32.2181 | 29.8716 | 24.9531 | 22.7519 | 21.3489 | 19.6875 | 21.2735 | 24.6756 | 25.6183 | 27.3799 | 30.0049 | 27.5659 | 23.8123 | 23.5829 | 24.4643 | 25.2748
61 | 23.5559 | 22.1081 | 21.9895 | 20.3512 | 25.0065 | 24.5339 | 22.7794 | 24.1696 | 24.6756 | 21.5708 | 17.6814 | 18.9756 | 19.2883 | 19.2367 | 20.7261 | 23.1457 | 23.6369 | 25.7685 | 24.1368 | 25.3818 | 26.2131 | 24.3671 | 26.6858 | 26.8025
62 | 26.171 | 26.7061 | 29.812 | 29.3705 | 30.7508 | 33.5824 | 34.0823 | 33.718 | 33.9882 | 32.0955 | 28.1938 | 28.1314 | 25.6652 | 23.7949 | 25.6168 | 25.866 | 24.1172 | 26.4991 | 24.966 | 23.4498 | 25.8986 | 26.6355 | 25.9467 | 27.0157
63 | 28.5413 | 30.3931 | 31.6767 | 31.9717 | 33.9573 | 33.783 | 31.6316 | 30.9571 | 31.2557 | 28.6286 | 22.5807 | 21.4406 | 18.9716 | 19.9978 | 20.7692 | 24.8533 | 25.253 | 21.0745 | 21.995 | 22.7267 | 18.6884 | 18.9721 | 21.2496 | 19.1081
64 | 18.7149 | 20.0379 | 24.4011 | 25.878 | 29.2693 | 27.321 | 26.5992 | 25.4292 | 26.1636 | 23.7763 | 24.0536 | 26.8418 | 24.0856 | 24.1465 | 24.1929 | 26.2413 | 27.1043 | 27.7055 | 29.0174 | 25.4147 | 21.5957 | 21.1144 | 22.2368 | 23.7069
65 | 23.6092 | 24.7049 | 26.4679 | 27.7389 | 30.6614 | 31.6146 | 32.5804 | 32.8064 | 34.2731 | 29.8639 | 25.4232 | 24.7385 | 25.4419 | 29.3928 | 30.5651 | 30.1053 | 29.0605 | 29.5828 | 27.5753 | 27.4654 | 25.4337 | 25.3113 | 25.1043 | 23.9722
66 | 21.253 | 21.77 | 24.0134 | 24.0324 | 25.384 | 25.0773 | 25.0195 | 25.4376 | 26.6839 | 27.1939 | 24.7716 | 23.2556 | 22.4553 | 25.4391 | 29.9797 | 31.1744 | 31.8001 | 30.5245 | 30.9424 | 28.695 | 28.7431 | 28.0313 | 27.3206 | 27.3901
67 | 28.5903 | 28.1957 | 29.2641 | 28.5776 | 27.9395 | 26.6134 | 26.1311 | 26.932 | 25.9369 | 24.331 | 20.9105 | 20.0421 | 19.6099 | 20.6155 | 21.6603 | 24.3888 | 25.2637 | 24.1321 | 20.5417 | 22.0702 | 23.3424 | 23.5115 | 21.1576 | 22.3144
68 | 23.4963 | 23.8113 | 25.8033 | 25.8485 | 28.1063 | 30.7597 | 30.5574 | 29.6472 | 29.8585 | 28.0861 | 25.4015 | 24.433 | 23.217 | 22.0328 | 22.3752 | 24.3247 | 24.1223 | 26.1644 | 29.6875 | 28.6511 | 28.1368 | 29.8393 | 28.8695 | 27.4399
69 | 29.6516 | 30.0152 | 31.8803 | 29.058 | 27.4215 | 27.2022 | 24.5944 | 25.4525 | 26.9352 | 24.3977 | 19.5601 | 19.6643 | 18.7811 | 19.3333 | 20.8667 | 21.8464 | 23.0574 | 23.749 | 25.1549 | 27.0623 | 24.7553 | 26.1829 | 24.5028 | 25.0081
70 | 23.1388 | 21.9729 | 22.4762 | 24.5487 | 27.5255 | 25.0658 | 23.028 | 23.3822 | 24.5337 | 21.1561 | 19.9323 | 23.5294 | 24.418 | 25.2048 | 28.4411 | 27.6252 | 26.9877 | 27.3262 | 31.0002 | 29.9652 | 29.1213 | 27.8865 | 29.101 | 25.912
71 | 26.6564 | 25.11 | 26.9953 | 27.8405 | 32.4569 | 34.2906 | 34.5746 | 34.2817 | 34.7274 | 32.2331 | 29.4785 | 28.8956 | 24.7746 | 24.9479 | 28.0346 | 27.9479 | 26.9071 | 26.6105 | 22.8634 | 22.8109 | 24.3356 | 21.5796 | 21.0602 | 20.7664
72 | 20.9736 | 20.9822 | 25.1754 | 25.7977 | 28.8652 | 28.3914 | 27.2705 | 26.959 | 25.5215 | 21.5241 | 17.6002 | 16.1005 | 16.8383 | 18.8008 | 23.0476 | 22.8431 | 20.563 | 20.0185 | 18.6143 | 18.0715 | 19.9142 | 20.4446 | 20.728 | 20.1246
73 | 23.8566 | 22.3456 | 26.2854 | 25.0979 | 28.8489 | 31.6822 | 29.919 | 30.3473 | 29.0153 | 23.8079 | 21.6109 | 22.0617 | 23.8757 | 25.9051 | 26.5151 | 25.7707 | 27.0156 | 29.0409 | 28.3754 | 28.9396 | 27.7661 | 27.8273 | 27.4544 | 24.8061
74 | 27.4245 | 27.0949 | 27.1811 | 26.8575 | 29.0819 | 27.8056 | 25.2562 | 24.2162 | 22.3056 | 22.5405 | 19.9697 | 19.4447 | 18.0476 | 18.6887 | 21.5525 | 19.8037 | 21.3312 | 21.9072 | 22.7801 | 25.7912 | 26.423 | 29.4061 | 27.0895 | 26.3636
75 | 30.5946 | 28.4988 | 30.5277 | 30.5705 | 30.794 | 29.3744 | 27.7117 | 28.1857 | 29.2482 | 26.4496 | 22.3405 | 23.8555 | 25.2105 | 24.7355 | 27.6534 | 29.839 | 25.1629 | 27.0408 | 26.3152 | 26.6584 | 25.7496 | 28.3093 | 28.4563 | 23.8656
76 | 26.5272 | 26.8657 | 28.476 | 26.9659 | 29.4726 | 32.2394 | 30.9706 | 30.1012 | 28.4315 | 23.9646 | 23.8032 | 23.1811 | 22.7257 | 25.521 | 27.9196 | 30.5925 | 28.4058 | 26.9009 | 24.2056 | 24.893 | 26.7852 | 28.2737 | 22.7838 | 19.173
77 | 21.1485 | 21.523 | 22.51 | 21.5417 | 23.4843 | 22.3453 | 21.9948 | 22.9185 | 22.606 | 19.048 | 20.4689 | 21.6159 | 22.2841 | 24.8774 | 28.3047 | 28.0426 | 27.5502 | 27.5406 | 25.5236 | 21.9871 | 20.6326 | 17.5093 | 20.7271 | 18.7201
78 | 19.0683 | 18.734 | 19.4966 | 23.1215 | 25.8062 | 25.8378 | 26.55 | 24.3048 | 23.449 | 21.849 | 21.7362 | 23.3668 | 20.3081 | 20.8039 | 22.8221 | 23.2192 | 22.9601 | 25.4586 | 24.0104 | 25.2523 | 24.8326 | 25.6136 | 25.5029 | 23.927
79 | 22.3676 | 21.8691 | 25.1404 | 25.0603 | 25.7266 | 26.9507 | 24.9239 | 26.0125 | 25.3191 | 21.1755 | 20.071 | 18.9232 | 17.7983 | 18.6616 | 19.7446 | 20.5377 | 20.7898 | 22.1026 | 20.2107 | 18.8116 | 21.8927 | 24.8359 | 23.4639 | 22.7246
80 | 24.9798 | 23.3471 | 24.8195 | 25.6834 | 26.1578 | 25.3435 | 23.7453 | 23.3712 | 22.6125 | 16.9035 | 16.3549 | 17.4426 | 17.5712 | 21.7204 | 26.5847 | 27.9571 | 26.7081 | 28.464 | 27.9181 | 26.2072 | 22.4562 | 23.9231 | 22.4111 | 20.8659
81 | 20.2319 | 20.9415 | 22.9422 | 24.361 | 24.3657 | 23.932 | 23.3585 | 22.9498 | 24.2345 | 20.9426 | 19.8976 | 18.1007 | 18.1383 | 19.8873 | 21.529 | 25.4698 | 23.2638 | 23.9344 | 24.1524 | 26.8083 | 23.4417 | 24.0141 | 23.8041 | 24.1851
82 | 25.5212 | 26.667 | 29.1626 | 28.7708 | 31.5444 | 32.0202 | 30.4568 | 28.7868 | 27.8326 | 22.0146 | 18.7376 | 18.7922 | 19.6137 | 22.3136 | 23.8438 | 26.007 | 26.3263 | 29.3562 | 27.7183 | 28.6071 | 29.4942 | 27.1139 | 29.3376 | 27.8582
83 | 26.5801 | 26.8888 | 27.9908 | 29.93 | 32.2065 | 31.9457 | 31.7385 | 29.3364 | 27.5476 | 25.5181 | 25.0171 | 25.3449 | 23.7783 | 23.7164 | 24.4234 | 22.4413 | 20.0416 | 22.2243 | 26.2322 | 26.2298 | 25.9299 | 22.4429 | 24.1009 | 21.2162
84 | 21.7437 | 20.1354 | 21.9822 | 22.0701 | 23.216 | 23.7317 | 22.9904 | 22.5248 | 23.2684 | 20.5357 | 19.5823 | 21.8168 | 23.8488 | 25.4549 | 26.3596 | 27.4446 | 28.7741 | 32.8803 | 28.5044 | 29.1114 | 26.5331 | 26.306 | 26.4539 | 20.5934
85 | 23.4639 | 22.56 | 23.7301 | 26.7171 | 29.5264 | 29.3522 | 29.0461 | 30.3679 | 29.9671 | 24.2364 | 24.3065 | 24.2962 | 24.7787 | 27.1624 | 29.0306 | 30.8158 | 31.8999 | 30.7067 | 31.2079 | 30.845 | 29.6202 | 27.7596 | 27.631 | 26.496
86 | 27.8545 | 28.1609 | 30.6626 | 31.1854 | 30.4896 | 30.8088 | 28.8589 | 27.9399 | 27.7021 | 27.9598 | 26.9944 | 26.0832 | 27.5398 | 29.0208 | 31.5915 | 29.6136 | 34.0174 | 34.8924 | 33.3789 | 30.6131 | 27.2103 | 27.2156 | 27.4031 | 23.9591
87 | 22.0925 | 21.641 | 24.5449 | 25.4793 | 26.4216 | 26.5134 | 26.2181 | 25.8496 | 26.7538 | 26.5708 | 25.6098 | 24.4304 | 22.3065 | 23.0511 | 27.2881 | 30.341 | 31.1459 | 29.2189 | 28.0256 | 28.081 | 31.1836 | 29.9052 | 28.7518 | 25.521
88 | 23.4234 | 24.0697 | 26.2183 | 26.9019 | 27.902 | 26.9736 | 24.3569 | 25.8435 | 25.3683 | 20.7302 | 20.2635 | 22.0552 | 20.8328 | 22.0682 | 22.6888 | 23.6273 | 24.5546 | 27.1755 | 26.5707 | 25.2629 | 22.5301 | 21.8254 | 23.1861 | 19.6835
89 | 20.3802 | 20.4837 | 23.6992 | 25.7894 | 26.039 | 26.4616 | 27.0131 | 26.2706 | 24.5486 | 23.0871 | 22.4429 | 22.4027 | 21.4573 | 23.1675 | 24.9728 | 27.141 | 25.4089 | 25.3665 | 22.5729 | 24.4831 | 19.7894 | 20.2527 | 21.5107 | 21.7063
90 | 23.6026 | 26.2108 | 29.1419 | 31.6816 | 32.9217 | 33.393 | 32.189 | 32.7039 | 31.4119 | 23.9507 | 20.598 | 19.0658 | 20.3967 | 20.6368 | 22.2363 | 27.0669 | 26.7831 | 28.7887 | 28.6684 | 31.2831 | 26.6772 | 24.223 | 25.3844 | 24.3664
91 | 24.7849 | 26.4513 | 29.24 | 28.4598 | 26.8395 | 28.8078 | 29.4387 | 31.015 | 28.5941 | 25.9667 | 24.6203 | 22.6263 | 21.6454 | 21.9382 | 27.1597 | 29.1342 | 29.1498 | 30.7776 | 31.3735 | 34.5929 | 30.4378 | 30.8989 | 31.3061 | 26.0906
92 | 26.8373 | 27.3136 | 30.0719 | 29.9662 | 29.3915 | 31.1856 | 29.4594 | 30.0852 | 29.5154 | 27.4415 | 23.8895 | 24.7028 | 23.7862 | 25.4998 | 26.873 | 29.4702 | 27.47 | 27.9972 | 25.9546 | 29.7578 | 26.3385 | 28.3326 | 31.105 | 28.6154
93 | 27.6502 | 26.7247 | 28.9906 | 29.8481 | 28.5233 | 30.3601 | 30.9608 | 28.6312 | 30.7564 | 28.7202 | 24.5592 | 24.0363 | 24.0924 | 25.3227 | 25.8034 | 26.3226 | 26.5481 | 26.4363 | 24.7758 | 23.5706 | 26.3385 | 24.3027 | 21.4475 | 18.5765
94 | 19.0359 | 20.746 | 22.6218 | 22.6632 | 22.5988 | 25.0175 | 26.8075 | 25.9716 | 26.1273 | 21.6518 | 21.2904 | 24.3683 | 24.0641 | 25.8283 | 25.5512 | 28.1352 | 29.997 | 29.1055 | 26.6402 | 30.1109 | 32.1506 | 34.9438 | 31.9395 | 28.6285
95 | 27.5752 | 27.5424 | 30.5063 | 29.8955 | 29.4473 | 30.5393 | 29.8175 | 27.684 | 29.0727 | 29.3123 | 28.6319 | 24.7459 | 23.9994 | 25.2074 | 26.6779 | 28.9663 | 25.3874 | 25.3453 | 26.0496 | 27.3444 | 26.5494 | 27.9465 | 28.8318 | 26.2842
96 | 25.5136 | 28.1539 | 31.8626 | 35.3407 | 33.2223 | 34.0384 | 33.141 | 32.6372 | 27.2775 | 21.1618 | 20.7197 | 21.8602 | 22.4263 | 23.4043 | 25.2935 | 26.3254 | 26.7049 | 26.8973 | 26.3937 | 30.426 | 29.8703 | 30.7629 | 28.2376 | 26.1962
97 | 26.7882 | 30.702 | 31.0713 | 32.2628 | 32.5227 | 30.5364 | 28.527 | 27.0423 | 25.1289 | 22.7199 | 23.5019 | 24.0422 | 21.3575 | 20.2391 | 24.6006 | 29.0447 | 30.0408 | 31.1201 | 31.8663 | 30.3495 | 27.7579 | 27.0132 | 26.6577 | 21.6453
98 | 19.6244 | 19.9448 | 21.5006 | 23.7819 | 20.4537 | 20.9311 | 23.6099 | 23.6784 | 21.738 | 21.7222 | 20.9296 | 21.9042 | 20.0312 | 19.935 | 21.1307 | 24.6007 | 24.1342 | 24.8389 | 22.2492 | 25.0044 | 22.9478 | 27.5401 | 30.2871 | 28.321
99 | 26.0037 | 27.3286 | 30.4265 | 33.166 | 33.6911 | 34.7019 | 34.4034 | 35.081 | 32.4326 | 28.6617 | 25.1386 | 22.7566 | 19.7332 | 20.3187 | 22.8258 | 25.7927 | 25.3801 | 26.3 | 28.4722 | 32.5401 | 33.9578 | 30.6217 | 27.7534 | 27.5219
100 | 26.9109 | 26.7308 | 31.0035 | 29.6838 | 24.7608 | 24.8901 | 23.6833 | 21.636 | 21.4267 | 20.8022 | 23.3139 | 26.5372 | 26.3659 | 25.2379 | 27.5283 | 29.3452 | 28.2732 | 30.006 | 29.5102 | 33.0756 | 31.5992 | 31.0007 | 27.2198 | 21.1856
101 | 19.7546 | 19.8213 | 21.7697 | 23.1086 | 21.5 | 23.3069 | 23.1234 | 25.3338 | 25.3417 | 24.4957 | 23.4237 | 26.777 | 24.2087 | 24.901 | 29.6111 | 30.9875 | 29.803 | 29.313 | 26.04 | 30.3602 | 31.213 | 30.8725 | 27.3884 | 22.9559
102 | 24.0731 | 22.6553 | 24.577 | 25.3271 | 20.4832 | 23.8651 | 25.5257 | 25.0679 | 22.9721 | 21.7269 | 21.734 | 22.2145 | 22.1903 | 20.4171 | 21.635 | 25.1066 | 27.5856 | 23.9258 | 24.6224 | 27.7718 | 29.7282 | 25.3202 | 24.2298 | 24.9601
103 | 23.6727 | 25.3938 | 27.1494 | 30.607 | 28.2149 | 27.6299 | 29.0171 | 28.0874 | 25.9477 | 22.6148 | 22.4213 | 24.0686 | 22.9312 | 20.9238 | 21.8333 | 23.9865 | 22.9237 | 24.4769 | 23.3091 | 27.6952 | 28.6112 | 30.2539 | 29.9571 | 24.9236
104 | 22.6188 | 25.1841 | 27.747 | 30.3052 | 29.1331 | 30.66 | 30.442 | 30.1567 | 30.0756 | 28.194 | 27.6933 | 30.9547 | 27.8742 | 26.1855 | 29.4167 | 32.1296 | 30.6283 | 32.03 | 33.004 | 36.054 | 32.3276 | 30.5174 | 30.4977 | 28.4289
105 | 28.1855 | 28.5932 | 29.2963 | 30.0096 | 25.5275 | 23.2303 | 22.3523 | 23.1878 | 19.073 | 16.7704 | 16.246 | 18.8211 | 19.0105 | 18.782 | 20.6617 | 24.3845 | 28.3798 | 31.3261 | 29.18 | 31.9254 | 31.6523 | 30.065 | 27.3772 | 22.5117
106 | 21.1317 | 22.0411 | 27.5124 | 30.0822 | 28.4226 | 28.3029 | 27.0447 | 27.4276 | 26.71 | 24.3654 | 21.5122 | 21.1525 | 18.7385 | 18.3776 | 19.2028 | 22.367 | 25.4427 | 23.4867 | 25.017 | 27.8656 | 26.8472 | 24.5682 | 24.114 | 20.818
107 | 20.7519 | 20.172 | 24.4086 | 27.2747 | 23.7735 | 22.9514 | 24.0946 | 25.5721 | 21.735 | 18.7062 | 17.5612 | 19.6584 | 18.6975 | 20.9402 | 22.7414 | 26.2364 | 24.3695 | 25.6052 | 26.6824 | 32.0587 | 28.9655 | 29.9763 | 29.6432 | 27.3002
108 | 28.3463 | 31.6705 | 34.8308 | 35.1364 | 31.42 | 31.0471 | 30.2285 | 29.488 | 24.5708 | 21.3814 | 20.8527 | 21.5968 | 21.6927 | 21.1161 | 23.4291 | 28.2176 | 30.0511 | 27.1855 | 26.9474 | 29.9611 | 27.5259 | 28.275 | 30.3377 | 27.4342
109 | 26.8679 | 30.3528 | 33.3077 | 35.7913 | 32.5291 | 31.5258 | 34.0487 | 32.6419 | 29.5669 | 27.2858 | 24.5158 | 21.7396 | 20.3389 | 20.0724 | 21.8639 | 25.8299 | 25.8664 | 27.2029 | 25.7891 | 25.6705 | 22.5722 | 19.6431 | 22.0918 | 19.8478
110 | 18.954 | 20.437 | 23.4575 | 27.3406 | 24.2925 | 23.7307 | 21.2373 | 18.2674 | 15.3081 | 17.1915 | 17.64 | 18.2453 | 18.9781 | 20.3979 | 21.0384 | 26.9279 | 26.1525 | 27.8778 | 28.3159 | 30.8308 | 29.1365 | 26.3882 | 22.4631 | 21.1621
111 | 18.202 | 20.145 | 25.0145 | 26.027 | 23.5512 | 24.9089 | 27.9499 | 27.2481 | 22.4959 | 23.1968 | 22.9046 | 22.7131 | 20.7223 | 20.6926 | 24.753 | 26.8277 | 27.212 | 30.8336 | 31.4618 | 32.1659 | 30.5804 | 26.7111 | 24.223 | 25.2575
112 | 22.2222 | 20.5413 | 21.6687 | 23.3339 | 21.2662 | 20.7737 | 20.6188 | 19.8926 | 17.3426 | 17.1103 | 20.2226 | 20.5755 | 20.5216 | 22.6696 | 26.7684 | 28.2197 | 28.0905 | 29.3348 | 29.6044 | 30.6231 | 30.5099 | 30.5625 | 28.0683 | 23.8364
113 | 22.3777 | 25.1395 | 27.7618 | 29.883 | 25.136 | 26.0808 | 27.6591 | 25.5412 | 22.4236 | 23.0914 | 22.5427 | 23.4217 | 24.9708 | 23.7246 | 26.2503 | 29.5651 | 31.2206 | 32.5361 | 32.0265 | 32.4563 | 31.3248 | 31.8239 | 28.154 | 25.9517
114 | 20.2578 | 21.5202 | 25.9591 | 29.8122 | 27.4256 | 27.9954 | 29.4526 | 29.0103 | 27.8885 | 29.1347 | 29.2412 | 26.6901 | 25.6388 | 25.9586 | 28.4106 | 33.9063 | 34.7583 | 34.9012 | 32.5909 | 34.5111 | 34.9603 | 32.1146 | 30.923 | 27.4307
115 | 25.9644 | 27.7081 | 30.7934 | 31.4562 | 28.0534 | 27.0307 | 25.9021 | 23.4793 | 22.2101 | 24.7905 | 26.2441 | 26.0082 | 24.2454 | 23.1488 | 23.6388 | 26.9718 | 28.4453 | 28.469 | 28.4961 | 26.2623 | 26.7776 | 24.5792 | 25.1606 | 22.5959
116 | 20.9358 | 26.0782 | 29.098 | 30.7388 | 29.4822 | 29.4002 | 29.952 | 26.5574 | 21.8471 | 20.8299 | 19.9606 | 20.554 | 22.8312 | 22.15 | 24.3118 | 24.8728 | 27.608 | 29.4133 | 28.7176 | 27.634 | 27.1916 | 26.6275 | 26.0653 | 24.9877
117 | 23.2494 | 22.6544 | 23.7629 | 25.7946 | 22.4482 | 20.7911 | 21.6246 | 20.8522 | 19.8277 | 18.8583 | 19.4655 | 21.1976 | 19.748 | 22.7508 | 25.4657 | 27.6628 | 30.9826 | 33.4766 | 34.4583 | 30.3156 | 28.2402 | 27.4735 | 22.2617 | 23.2557
118 | 22.685 | 26.4001 | 31.8668 | 31.9933 | 26.0439 | 26.0163 | 28.5508 | 25.5969 | 23.7376 | 22.3521 | 22.7555 | 24.0137 | 20.5211 | 20.8346 | 23.5176 | 28.54 | 28.9443 | 31.8015 | 31.6599 | 34.4428 | 32.7563 | 31.0193 | 26.7244 | 25.01
119 | 23.5074 | 23.1939 | 24.5563 | 26.7376 | 23.1263 | 22.1859 | 25.3025 | 26.1575 | 24.0121 | 24.0116 | 27.5659 | 27.4295 | 23.3631 | 24.4731 | 27.08 | 26.0876 | 27.3572 | 33.335 | 33.9532 | 29.9607 | 25.8673 | 27.5834 | 26.2895 | 21.3639
120 | 20.1341 | 21.2589 | 28.2154 | 29.3851 | 28.3648 | 26.1324 | 24.8577 | 24.5317 | 22.3883 | 24.2195 | 25.5374 | 26.2374 | 24.8091 | 27.8482 | 31.6153 | 32.4175 | 33.5333 | 31.5843 | 33.5995 | 28.7627 | 26.5912 | 22.4181 | 25.1403 | 21.5939
121 | 18.7412 | 19.5389 | 20.0493 | 21.6114 | 19.5502 | 20.3709 | 19.5714 | 17.5798 | 19.0295 | 20.4785 | 22.7177 | 21.6344 | 23.1771 | 26.1673 | 30.2981 | 30.7254 | 29.8573 | 34.0279 | 33.8699 | 28.8606 | 25.6519 | 21.0657 | 20.2624 | 19.7309
122 | 19.0489 | 17.901 | 18.8143 | 22.3898 | 23.7038 | 24.678 | 23.6914 | 22.7396 | 20.3294 | 18.711 | 17.7823 | 18.8608 | 20.4537 | 21.6216 | 23.82 | 23.0174 | 25.8359 | 23.6967 | 23.8191 | 26.2881 | 25.4712 | 23.336 | 21.7248 | 17.4082
123 | 15.0304 | 18.6283 | 24.6789 | 27.6492 | 27.341 | 28.0115 | 27.9605 | 24.0333 | 20.5569 | 19.1327 | 21.8712 | 21.4728 | 18.5468 | 18.072 | 19.3874 | 21.1252 | 25.4211 | 27.0255 | 30.8844 | 29.2508 | 28.9589 | 28.11 | 26.11 | 24.076
124 | 21.9946 | 19.2875 | 21.9848 | 23.3147 | 22.6252 | 22.8909 | 23.0713 | 21.4826 | 18.2781 | 17.4798 | 19.8894 | 21.1164 | 20.8657 | 20.6509 | 22.9524 | 26.504 | 26.2169 | 29.9665 | 28.0649 | 26.5623 | 26.5897 | 23.1571 | 23.89 | 22.9905
125 | 20.3789 | 19.2668 | 20.497 | 22.4329 | 20.8754 | 21.1366 | 22.8901 | 22.0275 | 21.191 | 20.555 | 19.853 | 20.7055 | 22.0716 | 24.4658 | 23.7644 | 25.8647 | 31.1757 | 31.0186 | 28.6462 | 30.4984 | 31.9391 | 29.2728 | 24.8894 | 24.1116
126 | 22.6897 | 20.4231 | 21.7658 | 26.4136 | 21.6209 | 22.5158 | 23.7779 | 22.2693 | 21.9291 | 22.2552 | 19.301 | 18.2518 | 19.4497 | 23.8315 | 27.4359 | 29.0815 | 34.1967 | 31.7074 | 34.2503 | 31.6793 | 31.314 | 29.6497 | 29.0856 | 29.6432
127 | 28.3632 | 26.2728 | 28.4908 | 29.0844 | 26.6928 | 26.6214 | 27.2686 | 23.6315 | 18.7972 | 19.2014 | 20.4452 | 23.0381 | 23.143 | 28.5158 | 28.5055 | 29.5225 | 29.2685 | 35.632 | 35.9993 | 36.2004 | 34.8028 | 30.2617 | 30.4102 | 30.0267
128 | 28.2926 | 27.182 | 28.4853 | 32.1456 | 28.4156 | 24.6266 | 24.0996 | 22.2723 | 20.3627 | 21.3572 | 23.5572 | 27.9365 | 25.2423 | 26.606 | 25.5359 | 29.5389 | 28.3911 | 30.0773 | 30.5174 | 26.8947 | 24.4097 | 27.9108 | 26.7753 | 24.9849
129 | 23.6399 | 23.1112 | 27.3912 | 30.1367 | 27.6846 | 26.3309 | 25.9539 | 25.2527 | 23.3038 | 20.3015 | 21.5428 | 23.8809 | 25.9134 | 25.8816 | 31.0296 | 30.4225 | 33.6867 | 34.7679 | 31.7048 | 31.5836 | 32.1091 | 31.1539 | 30.6326 | 31.697
130 | 26.2239 | 26.4288 | 28.547 | 28.7865 | 27.3044 | 26.0468 | 24.7682 | 22.0475 | 18.0115 | 16.4446 | 17.1812 | 17.7363 | 20.4825 | 26.9269 | 30.9389 | 34.1134 | 32.666 | 33.8686 | 35.9317 | 28.9307 | 27.5803 | 27.802 | 27.9742 | 25.8282
131 | 21.2038 | 19.3453 | 21.3819 | 22.2119 | 21.4495 | 18.3138 | 18.1476 | 17.4979 | 15.8535 | 18.9605 | 21.9046 | 23.8156 | 22.7828 | 24.044 | 25.8425 | 29.0838 | 32.176 | 34.5987 | 33.7318 | 33.3304 | 28.5606 | 27.0076 | 25.7002 | 23.275
132 | 19.8607 | 18.3324 | 21.386 | 23.8116 | 22.1242 | 23.1156 | 21.6302 | 21.1187 | 18.7066 | 16.1675 | 16.4105 | 16.559 | 17.1986 | 19.5207 | 23.75 | 24.7751 | 26.2763 | 29.9074 | 33.4068 | 28.1249 | 28.2549 | 28.7563 | 26.975 | 24.4827
133 | 22.179 | 19.3292 | 19.9779 | 21.6439 | 20.8159 | 19.1769 | 17.3028 | 18.2697 | 16.8166 | 16.3646 | 18.4708 | 18.3997 | 18.7575 | 22.2513 | 24.0143 | 30.4757 | 31.5367 | 33.4683 | 27.9686 | 25.3245 | 23.5628 | 27.0496 | 22.9899 | 20.6534
134 | 18.1426 | 17.5164 | 19.1549 | 23.4877 | 22.0055 | 22.1152 | 23.7249 | 21.2428 | 18.9671 | 18.4001 | 21.8189 | 19.5139 | 20.309 | 23.6668 | 25.7922 | 28.7523 | 31.5773 | 32.2038 | 33.7589 | 30.1498 | 28.5005 | 23.5716 | 21.6707 | 22.5331
135 | 21.0597 | 18.5153 | 20.5831 | 23.8313 | 23.4968 | 22.6555 | 22.4649 | 18.86 | 19.3784 | 18.2683 | 19.8622 | 19.3155 | 19.6367 | 23.6406 | 26.1302 | 26.7545 | 31.5863 | 29.6427 | 33.9436 | 34.8776 | 29.8966 | 31.6681 | 29.726 | 27.7191
136 | 22.6626 | 22.3706 | 24.7139 | 26.3212 | 26.456 | 25.2507 | 24.4152 | 19.9993 | 17.9457 | 18.8534 | 20.4322 | 23.6855 | 24.8588 | 25.5635 | 32.3855 | 29.4019 | 31.9059 | 32.8363 | 33.4303 | 32.5336 | 28.878 | 28.3312 | 23.9555 | 22.4942
137 | 22.3606 | 20.5986 | 22.0656 | 23.1827 | 23.7453 | 25.114 | 24.0399 | 23.2654 | 22.3759 | 21.558 | 23.4397 | 22.6465 | 19.1574 | 21.3103 | 25.7839 | 29.4827 | 25.8791 | 28.2682 | 30.521 | 33.4182 | 26.5897 | 28.7704 | 27.3327 | 27.3312
138 | 18.8103 | 16.0544 | 19.5306 | 23.0545 | 24.0408 | 25.0474 | 25.0063 | 22.0029 | 19.9379 | 19.1142 | 18.6977 | 19.2011 | 20.8988 | 22.6152 | 26.6806 | 27.588 | 27.6223 | 30.7591 | 34.7622 | 30.2612 | 27.7031 | 30.7037 | 28.4384 | 29.0418
139 | 26.5425 | 25.8633 | 25.9286 | 25.5056 | 25.637 | 26.3323 | 26.4774 | 21.7739 | 18.2452 | 16.1321 | 16.1787 | 17.4998 | 19.3398 | 22.4741 | 22.8403 | 24.8424 | 30.4727 | 29.248 | 28.3129 | 26.4682 | 25.2487 | 21.7017 | 19.4893 | 19.4187
140 | 18.5025 | 21.8332 | 25.574 | 24.8276 | 25.4071 | 23.6682 | 22.3983 | 18.1262 | 15.833 | 14.645 | 14.8776 | 14.6537 | 16.2715 | 19.9755 | 20.4549 | 23.2728 | 27.7015 | 30.8442 | 37.4174 | 35.5234 | 29.8784 | 30.6056 | 27.0986 | 24.3261
141 | 21.5115 | 18.9564 | 21.612 | 19.9575 | 20.8453 | 20.6705 | 20.5558 | 18.7948 | 16.8619 | 19.6062 | 22.048 | 22.9805 | 24.9704 | 25.2026 | 30.4183 | 32.2735 | 34.4342 | 37.8644 | 39.6624 | 35.635 | 31.6758 | 33.0431 | 31.1499 | 29.4566
142 | 21.5933 | 21.3184 | 22.7228 | 23.9288 | 23.6613 | 26.1334 | 24.7476 | 18.5546 | 17.7011 | 20.3763 | 23.2561 | 22.4904 | 21.3527 | 23.1184 | 23.7636 | 28.6228 | 34.2543 | 32.3071 | 32.8125 | 33.2669 | 31.7528 | 33.7698 | 29.6169 | 28.1125
143 | 25.0313 | 24.3327 | 25.0549 | 24.7039 | 21.4991 | 20.4438 | 20.0649 | 15.6965 | 15.0242 | 14.2034 | 13.7833 | 13.764 | 14.1897 | 19.022 | 22.6604 | 26.6518 | 27.4206 | 32.0255 | 33.7589 | 30.6039 | 28.0989 | 26.7413 | 21.9349 | 23.0365
144 | 21.1564 | 18.4048 | 22.7124 | 25.005 | 21.669 | 19.5393 | 18.0589 | 14.2206 | 12.8047 | 12.1949 | 14.6194 | 17.0836 | 20.0266 | 24.3058 | 29.4393 | 30.7708 | 30.8787 | 33.0187 | 33.6295 | 27.4487 | 23.617 | 22.4139 | 21.2541 | 21.249
145 | 20.4055 | 19.0695 | 18.7863 | 19.035 | 19.0644 | 19.0328 | 19.2829 | 14.3931 | 14.0874 | 14.228 | 14.6885 | 16.32 | 17.134 | 18.1886 | 19.9957 | 25.0842 | 31.0996 | 34.2992 | 32.152 | 27.5455 | 28.692 | 26.5948 | 26.1669 | 22.7896
146 | 20.1385 | 20.558 | 21.2395 | 20.8302 | 19.4048 | 17.438 | 16.772 | 15.0998 | 13.9432 | 15.4592 | 21.2466 | 21.3199 | 21.2007 | 23.0556 | 27.5346 | 27.3141 | 28.5843 | 32.8445 | 33.4981 | 29.9649 | 30.5626 | 27.925 | 25.7349 | 27.159
147 | 29.0499 | 28.3413 | 27.9733 | 26.3264 | 27.6118 | 26.2979 | 25.4058 | 20.3809 | 15.65 | 14.6852 | 15.8247 | 15.9648 | 15.7017 | 17.7065 | 22.3552 | 22.6054 | 29.2692 | 32.1554 | 33.6661 | 29.206 | 27.8148 | 28.37 | 25.8149 | 23.3211
148 | 22.6308 | 23.3269 | 25.5273 | 25.9404 | 24.4105 | 22.0375 | 20.4397 | 14.9646 | 10.5496 | 9.0601 | 10.1009 | 11.8191 | 16.2851 | 18.8362 | 24.4017 | 26.4947 | 29.8012 | 29.8234 | 32.084 | 33.4612 | 33.4704 | 27.5817 | 27.4603 | 25.56
149 | 21.3474 | 23.8773 | 24.8215 | 25.0917 | 21.2179 | 20.4844 | 19.8277 | 15.5743 | 12.7563 | 14.0533 | 18.259 | 20.8091 | 23.6124 | 27.0057 | 27.5693 | 33.7533 | 32.4136 | 30.9647 | 37.5475 | 34.824 | 32.1455 | 30.893 | 25.9324 | 20.9847
150 | 21.0348 | 25.7532 | 28.2876 | 28.898 | 26.6375 | 26.6507 | 22.4539 | 17.5511 | 14.4992 | 12.9057 | 13.5731 | 13.0205 | 16.1 | 22.8306 | 24.1507 | 23.6265 | 25.968 | 33.0204 | 33.2845 | 29.4888 | 30.5918 | 31.3307 | 22.5528 | 23.4881
151 | 25.0186 | 23.7156 | 25.284 | 22.5798 | 20.5261 | 19.6732 | 18.4363 | 12.3527 | 10.4587 | 11.4284 | 13.2054 | 13.3717 | 15.1366 | 22.9984 | 26.5811 | 28.2444 | 32.7289 | 34.6875 | 37.3287 | 35.0629 | 33.4631 | 33.5252 | 29.7381 | 29.872
152 | 21.5487 | 19.9538 | 22.9761 | 24.9874 | 24.0126 | 23.5964 | 19.1711 | 14.1576 | 12.1914 | 11.8666 | 14.9834 | 16.4358 | 17.1892 | 20.9343 | 24.616 | 27.4628 | 29.1364 | 32.0337 | 32.1691 | 28.1862 | 27.6904 | 26.5266 | 23.4982 | 23.2534
153 | 22.6807 | 20.9451 | 23.8709 | 24.7626 | 24.6165 | 22.9937 | 20.0328 | 13.0764 | 9.0208 | 8.9454 | 11.6055 | 15.4791 | 17.772 | 20.2505 | 21.6688 | 24.3439 | 27.4529 | 33.9589 | 35.7544 | 33.1841 | 30.6932 | 30.3379 | 27.4639 | 29.4761
154 | 25.7153 | 21.933 | 25.6671 | 21.7695 | 21.7047 | 18.6368 | 16.5272 | 12.6882 | 10.5819 | 11.2905 | 11.8592 | 11.9853 | 14.1668 | 17.9481 | 21.0214 | 20.7632 | 22.8566 | 27.675 | 29.6186 | 29.7787 | 27.4804 | 24.8817 | 20.575 | 21.3642
155 | 22.3776 | 24.0241 | 23.4071 | 22.7539 | 20.918 | 20.2186 | 18.0895 | 12.9123 | 11.4283 | 11.7675 | 11.9169 | 14.7105 | 14.7371 | 19.7568 | 26.116 | 27.443 | 29.0244 | 30.966 | 30.1446 | 27.8592 | 28.9925 | 27.7767 | 21.5846 | 23.195
156 | 19.2999 | 19.3202 | 21.8388 | 21.6644 | 20.9633 | 19.2087 | 20.4306 | 16.4503 | 14.4 | 13.2962 | 14.5587 | 15.9305 | 16.5099 | 20.1236 | 26.9744 | 25.7032 | 27.855 | 32.9645 | 33.2257 | 27.5918 | 27.1721 | 28.4271 | 28.5178 | 27.7313
157 | 23.9843 | 21.441 | 22.5711 | 23.1398 | 25.0288 | 25.5829 | 20.6559 | 15.7453 | 13.6639 | 14.8451 | 16.699 | 18.9266 | 17.1402 | 19.8507 | 32.3521 | 32.9461 | 30.0291 | 28.7808 | 33.4727 | 34.1609 | 29.8026 | 28.8669 | 29.6764 | 28.4455
158 | 30.4091 | 25.7926 | 27.9096 | 28.4119 | 26.0749 | 26.4521 | 23.8161 | 19.7645 | 19.4758 | 19.0593 | 17.5865 | 17.5892 | 17.4108 | 20.4845 | 28.5998 | 28.0449 | 28.7558 | 30.9685 | 31.8505 | 30.3251 | 33.6283 | 37.5233 | 33.7501 | 27.7541
159 | 30.134 | 28.4672 | 26.3203 | 25.031 | 25.2988 | 21.3225 | 19.6965 | 16.1849 | 13.397 | 12.471 | 13.0569 | 12.9006 | 16.2744 | 22.7289 | 26.1338 | 29.648 | 28.2407 | 26.2197 | 35.2987 | 32.309 | 31.2815 | 30.182 | 23.2339 | 24.4997
160 | 22.2009 | 22.9033 | 25.0331 | 24.6594 | 21.2846 | 21.1433 | 20.0584 | 16.7706 | 16.4137 | 17.0249 | 17.2688 | 18.5861 | 18.5407 | 18.4937 | 23.3035 | 22.7422 | 23.3041 | 29.0611 | 35.2406 | 33.1659 | 35.7399 | 34.6622 | 29.3937 | 29.1012
161 | 29.8898 | 29.0194 | 28.6898 | 28.8351 | 28.7316 | 25.1396 | 22.4683 | 16.3719 | 11.3754 | 11.4313 | 12.5492 | 12.9995 | 13.1517 | 15.1215 | 20.4878 | 22.5884 | 25.1348 | 32.3761 | 26.9497 | 24.6199 | 29.1514 | 28.4013 | 25.3215 | 24.2669
162 | 26.8994 | 28.3257 | 31.1732 | 29.2084 | 27.658 | 26.9988 | 22.1018 | 16.9221 | 11.4137 | 9.6954 | 9.5437 | 14.1042 | 18.231 | 18.1871 | 24.3364 | 27.0349 | 21.5274 | 26.8458 | 28.9959 | 26.4945 | 26.9681 | 30.5792 | 29.3501 | 25.7638
163 | 26.8881 | 28.6806 | 30.5245 | 29.9695 | 27.2838 | 23.6899 | 18.8031 | 13.7659 | 9.2619 | 7.9145 | 8.2343 | 10.2378 | 12.9691 | 16.853 | 22.9746 | 25.9206 | 26.4928 | 27.3343 | 29.4985 | 29.3501 | 31.0401 | 32.5562 | 30.6431 | 29.2615
164 | 31.0225 | 25.1611 | 25.9658 | 26.277 | 22.9064 | 22.0083 | 19.5045 | 14.8693 | 11.5932 | 13.0321 | 14.025 | 14.9685 | 14.1721 | 17.8848 | 23.9505 | 23.6308 | 24.4738 | 27.958 | 32.4821 | 25.6643 | 30.0397 | 33.3724 | 28.2187 | 26.8711
165 | 27.4061 | 25.3085 | 28.6124 | 26.9077 | 24.6343 | 24.5727 | 18.7361 | 11.9482 | 9.0491 | 9.0561 | 8.988 | 11.01 | 14.5652 | 16.8881 | 24.2296 | 23.2211 | 28.6169 | 33.1512 | 29.3842 | 32.8687 | 29.6363 | 31.0443 | 28.0838 | 24.6723
166 | 23.6806 | 25.4504 | 27.5647 | 27.9554 | 26.2517 | 22.0711 | 16.293 | 10.1562 | 7.5382 | 7.2373 | 7.8722 | 9.6933 | 11.9894 | 16.6164 | 21.9165 | 19.1691 | 18.8572 | 26.5062 | 28.9708 | 28.1473 | 33.6937 | 27.3938 | 26.212 | 26.9592
167 | 26.7491 | 27.1715 | 28.6828 | 28.4234 | 26.4678 | 25.151 | 20.1131 | 15.1947 | 12.9932 | 12.7033 | 10.9671 | 12.7573 | 16.7511 | 21.6221 | 28.4458 | 24.4075 | 26.2524 | 32.6079 | 33.0491 | 30.6601 | 31.342 | 33.7363 | 28.5798 | 26.4225
168 | 27.9362 | 31.6991 | 31.2122 | 31.682 | 29.3519 | 25.8621 | 22.9224 | 15.138 | 9.6455 | 8.9281 | 9.9489 | 11.2677 | 14.2754 | 20.2351 | 24.9565 | 22.1475 | 22.0971 | 25.4801 | 25.8234 | 24.6099 | 25.1212 | 28.6791 | 27.7496 | 29.7457
169 | 29.1358 | 29.1459 | 27.1555 | 28.3346 | 27.4073 | 23.4646 | 20.0149 | 16.4926 | 13.3451 | 12.1677 | 11.8903 | 13.4613 | 14.8536 | 15.2835 | 22.5872 | 23.2291 | 25.5197 | 24.4307 | 33.0258 | 33.7179 | 37.5227 | 35.393 | 28.638 | 29.5867
170 | 28.7803 | 26.9003 | 25.3181 | 25.4138 | 23.8746 | 22.7549 | 20.9495 | 17.2188 | 11.7539 | 10.0467 | 10.4129 | 10.3604 | 10.7709 | 15.6607 | 18.9972 | 20.6914 | 21.0547 | 25.1978 | 26.1945 | 26.5857 | 31.8687 | 36.411 | 33.0847 | 31.3588
171 | 30.2701 | 28.192 | 28.0932 | 26.7788 | 28.7152 | 24.2463 | 21.4157 | 16.0925 | 11.4798 | 10.9413 | 10.4457 | 14.0656 | 11.8885 | 14.7868 | 24.3241 | 24.2795 | 24.0088 | 28.1749 | 34.0059 | 31.5837 | 32.8022 | 33.1912 | 29.834 | 31.3986
172 | 31.6039 | 28.5869 | 28.4281 | 28.3832 | 24.9917 | 22.3819 | 19.1211 | 14.1905 | 8.5654 | 9.0684 | 9.6676 | 10.2391 | 11.4339 | 15.8235 | 22.5079 | 17.9595 | 26.0175 | 28.2288 | 31.795 | 29.8782 | 31.5968 | 33.4137 | 26.6845 | 25.8435
173 | 23.7915 | 19.0202 | 21.8649 | 23.9991 | 24.4691 | 24.1606 | 22.8924 | 17.165 | 11.263 | 9.7294 | 9.46 | 10.8562 | 9.7487 | 13.0056 | 19.4556 | 22.9025 | 23.6893 | 26.9868 | 26.3303 | 25.0452 | 27.0523 | 26.5962 | 24.186 | 27.7494
174 | 24.5215 | 22.042 | 21.8666 | 21.213 | 24.0173 | 25.5765 | 23.2227 | 17.8816 | 10.6644 | 9.3568 | 9.247 | 9.6218 | 8.4287 | 11.6378 | 18.6383 | 20.9803 | 23.8376 | 22.2295 | 27.7545 | 28.9905 | 30.4379 | 28.4127 | 20.8451 | 19.3743
175 | 26.1272 | 23.6919 | 24.6447 | 21.0581 | 22.0014 | 24.85 | 23.6604 | 15.7445 | 10.4219 | 9.0383 | 10.4287 | 10.1661 | 11.0384 | 14.3442 | 21.6319 | 26.9519 | 24.7051 | 31.5418 | 30.8063 | 29.7646 | 28.4615 | 28.9061 | 20.6332 | 19.059
176 | 19.4494 | 21.3423 | 20.5182 | 21.0567 | 20.9599 | 22.3768 | 21.0696 | 14.4528 | 8.5509 | 8.2821 | 8.7848 | 12.196 | 10.5649 | 14.7842 | 21.9126 | 25.8707 | 27.6692 | 31.1417 | 27.3903 | 28.5979 | 25.2769 | 28.8159 | 25.9838 | 23.8501
177 | 25.9731 | 23.5312 | 24.6912 | 24.5658 | 23.9372 | 21.8775 | 17.6567 | 13.5877 | 11.1095 | 11.8358 | 11.8687 | 13.6954 | 15.513 | 18.7797 | 20.0306 | 21.675 | 21.9786 | 30.0789 | 31.5449 | 27.4331 | 26.6583 | 26.0855 | 25.9998 | 24.8832
178 | 26.4218 | 22.4478 | 20.553 | 20.3188 | 21.941 | 21.0608 | 20.0333 | 10.5425 | 7.7459 | 9.1656 | 10.9862 | 11.3583 | 11.0338 | 11.744 | 15.2725 | 15.619 | 17.6519 | 25.941 | 28.7447 | 24.6909 | 28.0435 | 29.0629 | 23.3006 | 23.1741
179 | 27.5503 | 28.1872 | 26.6892 | 23.9036 | 22.4261 | 21.9262 | 19.8173 | 13.6425 | 7.3217 | 6.511 | 6.0835 | 6.2888 | 6.9377 | 10.4075 | 16.167 | 13.7663 | 17.774 | 26.0866 | 25.869 | 26.0815 | 27.2755 | 29.4285 | 24.2826 | 24.7565
180 | 25.2071 | 25.8484 | 23.9983 | 24.5738 | 26.0929 | 23.8472 | 18.7266 | 11.5723 | 6.9507 | 7.9461 | 7.6053 | 9.2305 | 10.8731 | 14.4412 | 16.9696 | 20.4693 | 25.4981 | 32.17 | 27.3392 | 27.872 | 24.409 | 28.6304 | 24.9571 | 26.3817
181 | 22.6726 | 21.3805 | 20.351 | 19.5649 | 23.5867 | 21.9259 | 17.5673 | 12.5684 | 7.241 | 9.4335 | 11.6315 | 14.0179 | 15.7291 | 19.8763 | 21.4857 | 23.5201 | 27.2548 | 31.6932 | 31.5174 | 32.8463 | 30.3026 | 31.1816 | 23.3232 | 23.1491
182 | 24.5126 | 24.2125 | 24.88 | 23.5701 | 23.7492 | 22.9658 | 20.8303 | 14.4276 | 8.563 | 8.2794 | 8.1015 | 10.8143 | 12.2826 | 14.2782 | 23.862 | 21.7516 | 24.4662 | 27.866 | 27.4648 | 28.0824 | 25.6175 | 28.9423 | 28.104 | 28.337
183 | 27.8032 | 24.9879 | 23.5712 | 22.711 | 22.5451 | 23.7256 | 23.9369 | 16.7701 | 9.7485 | 9.2304 | 9.6828 | 10.2617 | 8.8377 | 11.5481 | 17.5665 | 24.2293 | 22.6511 | 25.9376 | 30.6179 | 32.1576 | 32.7458 | 35.6111 | 36.6035 | 34.2316
184 | 28.5954 | 24.5217 | 23.7961 | 25.4583 | 30.6416 | 32.0245 | 28.3139 | 21.0592 | 14.4059 | 13.077 | 11.6835 | 8.97 | 8.1444 | 12.7366 | 12.5161 | 16.9059 | 25.6562 | 24.6483 | 30.2199 | 31.9563 | 31.7998 | 30.2312 | 31.6706 | 27.8564
185 | 27.3674 | 23.7101 | 27.5196 | 27.8711 | 27.9766 | 27.5992 | 23.4558 | 15.7175 | 10.0238 | 9.5489 | 10.7899 | 13.2559 | 12.0772 | 11.8303 | 13.4151 | 20.0822 | 23.2089 | 28.5221 | 28.8867 | 30.6083 | 30.062 | 30.037 | 29.8451 | 29.5355
186 | 30.8555 | 29.379 | 27.2863 | 26.6029 | 28.7983 | 26.4281 | 26.3858 | 20.3291 | 15.0968 | 14.7478 | 11.4962 | 10.449 | 7.5412 | 7.0542 | 15.9049 | 19.1684 | 19.1717 | 25.3244 | 34.3068 | 32.226 | 29.0025 | 28.5226 | 29.1358 | 27.7121
187 | 26.443 | 25.8291 | 21.3051 | 22.7729 | 22.9825 | 23.9559 | 23.9058 | 18.8052 | 9.4877 | 8.6853 | 8.0047 | 8.2952 | 10.7641 | 11.6283 | 17.5245 | 21.9648 | 17.17 | 23.1488 | 30.7699 | 29.2211 | 30.7901 | 31.4089 | 33.0288 | 31.3536
188 | 29.0393 | 24.5823 | 21.2965 | 24.2126 | 23.3337 | 25.4695 | 25.4239 | 21.2488 | 12.6768 | 10.9893 | 9.8272 | 8.965 | 7.1298 | 10.0897 | 17.3542 | 18.4773 | 21.0864 | 24.4388 | 28.6245 | 27.3839 | 23.3935 | 25.6618 | 25.4361 | 28.0897
189 | 28.5856 | 24.0803 | 22.7643 | 22.1909 | 20.1062 | 22.7042 | 22.1502 | 17.6924 | 11.2021 | 10.8535 | 10.4864 | 9.8177 | 9.0053 | 11.7147 | 13.5818 | 16.3828 | 17.0174 | 28.8253 | 26.5284 | 27.6095 | 24.9041 | 28.5618 | 26.3187 | 26.5875
190 | 21.7451 | 20.4939 | 21.9503 | 22.4332 | 19.6034 | 22.5922 | 21.1742 | 14.9858 | 8.2801 | 8.8262 | 8.8356 | 8.2389 | 9.2149 | 9.4463 | 12.3988 | 16.3582 | 17.0858 | 27.1852 | 27.4223 | 22.7025 | 24.9321 | 32.1532 | 29.913 | 28.0157
191 | 30.3345 | 27.0183 | 23.8391 | 23.4944 | 25.448 | 24.1557 | 23.7845 | 18.5983 | 11.8344 | 12.4804 | 11.6422 | 11.4832 | 8.6179 | 9.1308 | 13.2853 | 14.2819 | 18.0851 | 20.2621 | 29.5266 | 26.7278 | 28.9465 | 24.5673 | 26.0905 | 28.344
192 | 25.9589 | 24.9522 | 22.5555 | 25.3736 | 28.9916 | 30.0375 | 29.1754 | 22.4825 | 12.8049 | 11.484 | 8.2959 | 7.0519 | 6.075 | 6.0946 | 7.8263 | 15.8382 | 20.3591 | 22.7674 | 31.3218 | 28.9449 | 25.579 | 29.7077 | 25.3504 | 25.455
193 | 23.5633 | 24.0391 | 21.7428 | 20.333 | 21.1268 | 23.9764 | 24.2304 | 16.622 | 7.3434 | 5.5223 | 5.437 | 6.263 | 6.1088 | 8.4438 | 16.2233 | 16.7402 | 15.844 | 22.9576 | 25.9569 | 27.0447 | 24.9619 | 22.4759 | 22.194 | 23.947
194 | 23.1931 | 20.8958 | 20.177 | 21.5737 | 25.8138 | 27.1618 | 26.5026 | 18.4323 | 7.9645 | 7.1717 | 6.4681 | 7.6962 | 6.5695 | 9.537 | 12.1958 | 16.3003 | 18.1159 | 26.635 | 26.2791 | 25.3789 | 20.9508 | 23.3448 | 24.1535 | 22.1387
195 | 22.4117 | 17.6567 | 18.6755 | 20.7108 | 23.1696 | 22.5295 | 23.0262 | 16.3131 | 9.8259 | 9.7698 | 9.4914 | 7.5455 | 4.6938 | 6.126 | 11.684 | 15.5226 | 18.8206 | 16.8502 | 21.2363 | 22.1022 | 23.0302 | 20.9101 | 24.5571 | 24.5052
196 | 26.8993 | 22.9195 | 23.6736 | 23.8417 | 24.2064 | 26.2531 | 24.2685 | 16.8338 | 10.331 | 9.1322 | 8.9374 | 8.7988 | 9.3594 | 9.7709 | 18.6702 | 19.1103 | 25.8869 | 25.5224 | 27.7655 | 28.7901 | 24.3208 | 25.1214 | 25.0866 | 26.0771
197 | 27.5824 | 27.3661 | 23.4817 | 23.594 | 24.8109 | 29.0335 | 28.7417 | 20.6273 | 11.6638 | 10.5944 | 10.1093 | 9.1332 | 11.5865 | 10.6971 | 13.5872 | 15.5164 | 19.2348 | 24.4425 | 27.2289 | 30.3056 | 27.984 | 33.2309 | 32.6336 | 28.534
198 | 30.994 | 28.0127 | 27.808 | 28.9648 | 28.6326 | 30.599 | 29.0882 | 21.611 | 11.3429 | 10.2252 | 9.8191 | 9.6473 | 10.6123 | 9.0863 | 9.6169 | 14.7448 | 16.8136 | 21.9504 | 25.3031 | 26.8462 | 26.0118 | 29.3169 | 26.5156 | 28.3717
199 | 28.7601 | 23.9196 | 23.5901 | 27.0791 | 27.7647 | 29.0162 | 28.2062 | 19.0349 | 10.0348 | 9.2337 | 7.0477 | 6.4603 | 7.0567 | 7.7493 | 12.1385 | 18.3649 | 18.0781 | 29.4289 | 33.9309 | 25.7738 | 25.9697 | 27.7323 | 27.71 | 27.1482
200 | 30.7149 | 25.9973 | 21.8017 | 23.0767 | 23.0725 | 23.9161 | 24.0195 | 17.3808 | 8.4499 | 7.5686 | 6.3961 | 6.3506 | 6.1934 | 8.3894 | 11.7301 | 20.3096 | 20.7707 | 23.075 | 27.0031 | 24.3559 | 23.596 | 23.5598 | 22.0437 | 25.8663
201 | 26.5283 | 24.9937 | 22.2528 | 22.6594 | 20.2503 | 21.2699 | 17.9186 | 13.1283 | 6.252 | 4.9293 | 5.5243 | 6.446 | 9.4102 | 7.2012 | 13.6358 | 21.3155 | 24.0913 | 24.4491 | 31.2981 | 28.3085 | 28.7212 | 26.3501 | 24.5726 | 25.188
202 | 24.6566 | 21.7888 | 18 | 19.409 | 19.5909 | 20.3068 | 18.3603 | 15.0664 | 8.3354 | 7.4398 | 6.1767 | 7.3009 | 7.6245 | 10.9846 | 10.3896 | 15.7348 | 21.3433 | 30.9338 | 26.9147 | 28.0535 | 26.3743 | 30.8531 | 29.7014 | 28.099
203 | 27.5827 | 22.7345 | 18.5004 | 19.6375 | 20.5878 | 22.765 | 20.9358 | 17.3679 | 10.2368 | 7.987 | 7.7371 | 8.1285 | 7.2681 | 7.4645 | 9.4974 | 18.3152 | 20.0873 | 23.5989 | 27.2227 | 25.2432 | 28.5986 | 25.5926 | 27.1833 | 27.0308
204 | 19.1367 | 19.3591 | 18.6513 | 21.9612 | 20.9688 | 22.7136 | 24.5556 | 18.4682 | 11.6912 | 10.4491 | 9.8674 | 12.0491 | 9.7048 | 13.2804 | 15.1973 | 19.8077 | 21.8798 | 22.9386 | 26.971 | 26.0863 | 23.0063 | 27.4507 | 19.8091 | 21.7391
205 | 18.9837 | 18.2718 | 17.7651 | 20.1864 | 22.6172 | 23.6948 | 22.461 | 18.2603 | 9.7651 | 10.1764 | 9.7763 | 9.8303 | 7.597 | 8.8115 | 11.4734 | 21.0113 | 17.4386 | 22.6556 | 24.669 | 25.8025 | 23.8341 | 24.8661 | 24.6939 | 26.1031
206 | 25.8092 | 19.528 | 17.9604 | 18.6702 | 21.4051 | 20.7989 | 19.8113 | 14.793 | 9.3924 | 12.6923 | 13.6236 | 11.7647 | 10.5876 | 8.0898 | 11.8282 | 16.9702 | 19.5771 | 21.5202 | 24.3473 | 26.5205 | 25.1262 | 31.0803 | 24.6851 | 25.1027
207 | 26.733 | 23.4553 | 20.2039 | 17.8768 | 19.8287 | 21.4837 | 20.2808 | 14.9944 | 9.3251 | 9.4797 | 8.8948 | 9.2666 | 10.5148 | 8.9556 | 12.3723 | 16.8947 | 19.9089 | 25.445 | 21.1373 | 29.1187 | 22.4342 | 23.635 | 25.0665 | 25.846
208 | 27.9251 | 22.2202 | 19.53 | 22.1861 | 24.1314 | 23.607 | 21.9913 | 16.3541 | 10.2412 | 8.6154 | 7.9984 | 10.1368 | 9.1837 | 6.8759 | 12.8483 | 14.5193 | 15.7733 | 18.6412 | 21.9919 | 22.636 | 24.1427 | 22.837 | 20.1267 | 21.1977
209 | 21.7431 | 18.194 | 17.511 | 17.4941 | 20.103 | 21.5359 | 21.1398 | 15.8474 | 10.2374 | 10.6823 | 8.5267 | 6.2787 | 6.8152 | 6.0729 | 12.8135 | 17.7287 | 22.894 | 23.2163 | 24.6785 | 25.6202 | 26.5131 | 24.3106 | 21.3082 | 23.3244
210 | 21.7075 | 20.2694 | 18.5464 | 18.125 | 16.0221 | 14.4198 | 13.7725 | 14.281 | 10.9211 | 10.3424 | 8.5529 | 8.8068 | 7.4738 | 11.6549 | 16.5907 | 23.3758 | 17.8632 | 20.7538 | 25.3049 | 31.1472 | 25.9899 | 24.3836 | 20.8219 | 23.1727
211 | 24.3596 | 22.0995 | 22.8412 | 24.8697 | 26.2436 | 25.9759 | 21.1735 | 18.4593 | 11.7265 | 11.9925 | 9.9301 | 6.498 | 6.0232 | 9.1216 | 11.544 | 13.9546 | 17.8826 | 18.1221 | 23.8784 | 24.489 | 25.1474 | 23.2229 | 24.3946 | 21.6088
212 | 20.576 | 19.1966 | 19.9195 | 18.9365 | 19.2144 | 19.9278 | 19.1457 | 16.4621 | 9.735 | 10.6025 | 11.3191 | 10.5815 | 9.1373 | 10.3357 | 12.35 | 15.9662 | 13.063 | 18.981 | 23.3905 | 23.0818 | 25.1056 | 26.6051 | 24.0289 | 20.0784
213 | 23.2448 | 17.906 | 19.7584 | 21.456 | 25.1457 | 26.5272 | 23.5158 | 16.0447 | 8.5743 | 7.0618 | 7.1665 | 8.1819 | 11.2822 | 12.4618 | 11.9199 | 15.6482 | 24.0926 | 20.7906 | 24.0068 | 28.2975 | 23.1053 | 21.7858 | 20.9501 | 19.525
214 | 22.5354 | 21.9214 | 22.2911 | 21.3375 | 21.5863 | 21.0136 | 23.031 | 19.9756 | 10.7384 | 9.8946 | 8.3482 | 7.7311 | 8.3851 | 9.6704 | 13.1372 | 15.3733 | 18.6036 | 20.2613 | 22.5742 | 25.3464 | 24.8157 | 22.7743 | 26.7505 | 24.1353
215 | 22.8772 | 21.5287 | 19.7938 | 17.7571 | 19.877 | 19.7653 | 21.3557 | 17.3985 | 12.1856 | 11.6183 | 11.1093 | 10.1921 | 12.3247 | 12.3292 | 15.1326 | 19.1782 | 23.3662 | 23.6202 | 23.3653 | 24.5923 | 23.1847 | 24.4471 | 22.5445 | 25.1292
216 | 22.9476 | 21.2653 | 21.2578 | 20.5784 | 20.5268 | 20.504 | 19.6191 | 13.9889 | 8.822 | 9.1769 | 9.4496 | 8.5408 | 9.0082 | 10.5779 | 15.3893 | 19.4062 | 17.634 | 22.4584 | 24.6335 | 26.3487 | 26.749 | 23.99 | 24.6906 | 19.8462
217 | 18.7657 | 18.498 | 17.5743 | 19.1812 | 19.7247 | 21.4443 | 22.3417 | 17.1257 | 11.4555 | 12.1971 | 10.9121 | 8.7742 | 7.0189 | 12.4977 | 14.0429 | 16.1224 | 20.4045 | 24.0771 | 23.3463 | 21.5733 | 22.9782 | 23.4054 | 23.1614 | 20.6517
218 | 22.9326 | 24.018 | 21.99 | 19.1682 | 16.8498 | 16.7279 | 18.2015 | 17.5312 | 13.2062 | 12.2271 | 11.3331 | 10.0596 | 7.8398 | 10.3444 | 13.665 | 16.6714 | 16.3752 | 15.9984 | 23.8039 | 25.8798 | 23.6117 | 23.0017 | 25.2038 | 20.9998
219 | 25.5369 | 22.9802 | 19.1262 | 19.9777 | 22.0484 | 21.9098 | 20.1293 | 16.6363 | 9.9479 | 9.6417 | 8.4105 | 8.6004 | 8.3863 | 10.6098 | 14.9066 | 19.4189 | 18.4812 | 24.3833 | 19.2069 | 23.6212 | 22.8778 | 23.3287 | 18.9046 | 19.0567
220 | 20.8729 | 18.662 | 19.2364 | 20.676 | 22.0178 | 22.7217 | 22.7677 | 19.348 | 13.208 | 13.198 | 10.6445 | 8.9073 | 7.0719 | 5.7425 | 11.2123 | 12.6625 | 11.0498 | 19.337 | 19.8731 | 21.1588 | 22.5248 | 25.075 | 22.7155 | 19.0729
221 | 22.3803 | 20.9338 | 21.6181 | 21.0339 | 20.9349 | 24.6184 | 22.4688 | 18.1892 | 10.5564 | 8.7198 | 8.5911 | 7.9999 | 6.8981 | 9.2297 | 11.4455 | 12.8345 | 12.6344 | 16.1281 | 21.8063 | 25.0574 | 21.6921 | 22.7479 | 19.0722 | 17.5426
222 | 17.7064 | 18.4077 | 20.6184 | 15.8672 | 13.2987 | 14.9326 | 17.43 | 13.3293 | 7.2833 | 6.9175 | 5.7215 | 7.2288 | 8.0174 | 13.5966 | 16.6637 | 18.2946 | 19.8722 | 21.0668 | 22.9391 | 24.3281 | 24.63 | 27.4305 | 20.8961 | 17.5724
223 | 21.8683 | 22.243 | 20.2773 | 19.5358 | 15.8507 | 18.4441 | 18.6248 | 16.5324 | 12.2915 | 11.6269 | 10.8476 | 10.0332 | 11.0452 | 13.286 | 11.4528 | 16.052 | 14.99 | 21.9258 | 20.3118 | 30.4862 | 23.9666 | 22.246 | 24.09 | 21.9291
224 | 22.5774 | 17.9647 | 17.6641 | 17.9743 | 18.702 | 18.2402 | 17.8923 | 15.9414 | 11.329 | 10.9778 | 10.2183 | 9.802 | 11.6571 | 12.588 | 11.7646 | 13.3237 | 15.3209 | 16.5733 | 14.8728 | 19.4179 | 23.3396 | 23.7225 | 19.732 | 15.823
225 | 24.509 | 24.2176 | 20.6796 | 20.4588 | 20.8226 | 19.0931 | 17.891 | 14.9625 | 8.8832 | 10.0524 | 6.9028 | 7.0883 | 9.6208 | 13.0892 | 15.7233 | 16.7221 | 16.6512 | 18.0562 | 23.9137 | 24.614 | 24.587 | 26.7742 | 24.535 | 16.2163
226 | 21.7183 | 22.4232 | 21.4066 | 18.097 | 18.2753 | 18.405 | 18.5373 | 15.6319 | 9.8744 | 8.9494 | 8.8265 | 9.9938 | 10.6438 | 10.0469 | 11.013 | 14.2456 | 16.6231 | 18.848 | 17.7608 | 21.1484 | 26.8073 | 26.1081 | 23.1103 | 23.7699
227 | 26.1597 | 23.8918 | 22.645 | 21.8073 | 20.6029 | 22.9156 | 22.4048 | 21.1239 | 15.4493 | 16.2541 | 14.1942 | 14.3198 | 14.0911 | 14.8025 | 11.1895 | 16.2198 | 18.0244 | 21.4276 | 19.395 | 21.2774 | 27.4082 | 29.4198 | 30.1104 | 28.1936
228 | 24.3142 | 22.4014 | 24.3495 | 23.0648 | 20.0567 | 20.4878 | 21.288 | 18.5015 | 13.3922 | 11.2322 | 9.1307 | 10.0635 | 9.9193 | 12.6827 | 9.688 | 19.1153 | 18.5208 | 20.3625 | 19.5286 | 24.6469 | 22.755 | 24.2589 | 25.9372 | 24.0635
229 | 23.7206 | 22.771 | 22.9329 | 22.5634 | 23.0422 | 18.5055 | 18.1863 | 15.0222 | 8.4366 | 6.4607 | 5.1615 | 4.6489 | 5.8925 | 11.9821 | 13.2339 | 19.7204 | 21.3533 | 20.3434 | 19.7142 | 23.957 | 25.85 | 25.0332 | 26.1996 | 25.7391
230 | 25.034 | 25.0138 | 28.1903 | 26.3533 | 26.5904 | 24.6026 | 23.9519 | 22.8797 | 16.5761 | 15.5233 | 14.3292 | 12.0869 | 11.9525 | 10.8557 | 11.781 | 12.9671 | 19.0492 | 14.5579 | 15.5253 | 24.3536 | 23.5904 | 21.1593 | 15.9535 | 20.2331
231 | 19.7398 | 18.4285 | 22.4379 | 22.8969 | 23.186 | 20.5969 | 21.0443 | 19.7645 | 14.0799 | 10.528 | 9.4232 | 10.3953 | 11.5401 | 11.9782 | 12.703 | 14.89 | 15.1747 | 17.6757 | 19.089 | 20.6563 | 21.1211 | 22.351 | 22.9719 | 20.3483
232 | 20.0747 | 20.535 | 22.2145 | 24.5314 | 21.9287 | 21.0303 | 20.5532 | 20.1083 | 14.4766 | 10.5558 | 9.5101 | 9.8596 | 9.7219 | 11.9242 | 11.8829 | 13.5833 | 12.6587 | 11.1819 | 14.6562 | 19.1577 | 21.5908 | 27.1686 | 25.9925 | 22.7683
233 | 22.4867 | 24.1134 | 25.7395 | 24.8501 | 24.347 | 22.6228 | 22.6079 | 18.009 | 13.67 | 13.7595 | 13.0276 | 9.6692 | 8.3398 | 9.5455 | 10.2858 | 11.3569 | 13.0854 | 15.2552 | 21.9145 | 26.8074 | 25.3934 | 24.093 | 25.6479 | 27.7381
234 | 30.1892 | 28.5723 | 29.6517 | 26.6239 | 24.8213 | 24.0109 | 23.2732 | 20.3431 | 15.3343 | 13.4948 | 12.2482 | 11.0419 | 11.5545 | 12.0565 | 14.3497 | 12.6509 | 17.602 | 19.6386 | 20.0937 | 21.8821 | 18.7319 | 19.3714 | 22.2951 | 25.2571
235 | 24.9596 | 24.1488 | 24.6529 | 25.7068 | 25.0191 | 23.8517 | 23.178 | 20.8704 | 14.072 | 13.67 | 10.7237 | 10.3311 | 10.1816 | 12.3133 | 12.6941 | 15.5844 | 19.7654 | 20.2404 | 24.0081 | 28.9023 | 25.5378 | 29.3214 | 27.3693 | 25.7715
236 | 27.0226 | 24.8746 | 24.1826 | 25.6193 | 27.0854 | 23.4206 | 20.8176 | 20.2414 | 14.557 | 12.7683 | 11.9838 | 11.4874 | 9.454 | 11.5361 | 14.6935 | 13.7339 | 18.542 | 19.4031 | 22.2385 | 31.5729 | 27.4253 | 27.5062 | 24.4493 | 22.7045
237 | 21.3816 | 22.0824 | 24.5231 | 25.1877 | 23.0049 | 22.2687 | 21.6412 | 20.7054 | 15.3253 | 13.6436 | 11.7089 | 10.5518 | 8.2035 | 10.9453 | 9.2024 | 16.0378 | 19.4609 | 18.8813 | 21.5011 | 27.8998 | 24.7828 | 24.7452 | 24.6661 | 22.4556
238 | 21.4662 | 21.0801 | 18.2793 | 19.4361 | 20.9605 | 19.6577 | 21.3819 | 19.7838 | 12.8766 | 11.3715 | 10.2841 | 7.9171 | 7.4229 | 11.1286 | 10.7784 | 14.9052 | 17.4907 | 18.2558 | 20.8092 | 24.1475 | 27.0624 | 26.1174 | 29.9951 | 27.2426
239 | 22.4157 | 24.6523 | 23.4749 | 24.0443 | 23.6622 | 21.9788 | 20.6373 | 17.1533 | 11.2597 | 9.4911 | 10.6035 | 12.1103 | 11.922 | 13.4277 | 11.7018 | 13.8597 | 16.5206 | 17.5011 | 19.0183 | 22.5355 | 26.1626 | 25.6393 | 24.3781 | 22.0536
240 | 22.6313 | 22.6654 | 23.3186 | 23.9616 | 23.0433 | 21.4206 | 22.0148 | 21.4559 | 13.6347 | 9.3555 | 6.2705 | 5.0366 | 6.6082 | 9.6657 | 11.8577 | 16.0894 | 17.7654 | 19.4792 | 21.1046 | 27.1986 | 24.4833 | 23.4692 | 21.6114 | 20.1426
241 | 18.5493 | 20.3169 | 22.4279 | 21.1094 | 19.3953 | 21.015 | 22.89 | 20.5174 | 13.117 | 11.5282 | 10.1973 | 9.1023 | 9.3482 | 8.5685 | 10.548 | 13.3698 | 15.3189 | 16.2069 | 15.491 | 20.0876 | 23.2722 | 26.4093 | 25.9539 | 28.6788
242 | 29.376 | 26.4012 | 21.7784 | 19.9953 | 24.2548 | 22.596 | 22.6497 | 22.4818 | 17.0394 | 12.4263 | 11.5368 | 8.8979 | 10.6196 | 13.4141 | 15.4799 | 17.8691 | 21.6816 | 21.0491 | 22.904 | 30.8492 | 28.655 | 26.8578 | 28.0612 | 25.6098
243 | 24.8221 | 24.8142 | 23.7453 | 20.8772 | 21.5514 | 22.8659 | 24.5322 | 23.4482 | 16.7921 | 13.6295 | 12.5245 | 12.1146 | 11.1951 | 14.4791 | 15.0156 | 14.6864 | 17.5395 | 17.7206 | 23.0863 | 30.0977 | 22.5776 | 26.9151 | 26.6253 | 27.903
244 | 24.2128 | 21.8267 | 21.5249 | 19.4951 | 17.5712 | 18.19 | 18.2857 | 17.273 | 13.4567 | 12.4487 | 10.8532 | 9.3767 | 10.4166 | 14.8071 | 16.2421 | 16.5299 | 17.7517 | 19.3168 | 18.3077 | 26.2269 | 30.0796 | 30.3313 | 25.2385 | 26.4757
245 | 23.1725 | 24.5855 | 25.1545 | 26.3287 | 26.553 | 24.8415 | 25.3326 | 23.2504 | 16.3791 | 12.0313 | 7.9508 | 6.7101 | 7.805 | 9.5658 | 11.6778 | 12.6971 | 14.9467 | 16.3644 | 24.215 | 27.0489 | 29.1893 | 28.7387 | 25.8333 | 25.7001
246 | 23.5276 | 23.2923 | 23.7668 | 24.9889 | 26.8892 | 25.2584 | 23.7897 | 21.1291 | 16.7943 | 12.6186 | 9.1061 | 9.336 | 10.6424 | 9.9566 | 10.477 | 18.1059 | 20.6687 | 21.2024 | 24.914 | 28.6876 | 34.2254 | 32.0367 | 31.8339 | 27.8684
247 | 24.3973 | 23.5535 | 24.7169 | 23.6417 | 21.2785 | 19.6122 | 19.4059 | 18.6373 | 14.3092 | 10.629 | 8.5699 | 8.7498 | 10.5772 | 12.1345 | 14.8103 | 18.9764 | 19.2108 | 20.0538 | 24.6664 | 28.2779 | 28.0012 | 31.8415 | 33.9973 | 29.6574
248 | 28.2102 | 25.0095 | 24.7622 | 28.5739 | 28.6408 | 26.0478 | 26.5119 | 25.3599 | 18.7557 | 13.5713 | 10.5254 | 9.5103 | 12.1005 | 12.0446 | 11.4658 | 14.1396 | 20.7184 | 20.9667 | 26.684 | 32.428 | 31.5489 | 26.8007 | 24.8965 | 25.8124
249 | 26.1795 | 26.3822 | 28.2353 | 25.5726 | 25.3766 | 24.0708 | 24.3144 | 24.3625 | 19.5075 | 16.2678 | 14.7803 | 13.3865 | 11.5935 | 12.9747 | 14.1822 | 16.0969 | 16.2427 | 19.3833 | 27.0838 | 32.7272 | 26.7662 | 25.9409 | 29.0012 | 32.0631
250 | 27.0315 | 26.489 | 26.6884 | 24.5235 | 25.0719 | 23.3349 | 23.7261 | 22.6914 | 19.9656 | 18.3017 | 15.9709 | 12.3555 | 12.7703 | 14.7641 | 17.0204 | 18.3788 | 22.1316 | 21.267 | 20.561 | 27.2036 | 27.6011 | 25.5219 | 27.4687 | 26.424
251 | 25.1621 | 26.7733 | 26.1002 | 25.122 | 22.83 | 19.8422 | 20.3072 | 20.7781 | 16.297 | 13.0459 | 11.7298 | 10.8596 | 11.2722 | 13.8485 | 16.7489 | 15.8465 | 18.1358 | 21.1808 | 20.2818 | 26.8688 | 28.6783 | 27.6842 | 26.8827 | 28.7851
252 | 25.2317 | 28.4996 | 26.889 | 24.2539 | 24.2451 | 23.4388 | 23.6498 | 22.2065 | 15.4607 | 12.2112 | 10.1873 | 9.6908 | 10.6542 | 12.6461 | 17.3338 | 18.4378 | 24.1676 | 21.6335 | 24.3661 | 31.1581 | 31.3223 | 28.9473 | 27.1696 | 25.7469
253 | 23.4995 | 25.9077 | 27.0632 | 28.3402 | 26.246 | 24.8598 | 26.5067 | 25.9261 | 21.1219 | 19.2124 | 17.0136 | 16.8456 | 16.4067 | 17.6858 | 16.2632 | 19.4472 | 23.5676 | 23.0551 | 26.7085 | 30.4385 | 28.9687 | 31.8427 | 27.6974 | 24.5834
254 | 24.3899 | 25.0924 | 26.7636 | 25.7356 | 26.4871 | 24.9091 | 25.9017 | 24.9603 | 20.9791 | 19.4926 | 17.4605 | 16.3296 | 17.1366 | 16.4808 | 18.4685 | 17.2249 | 19.1641 | 20.3593 | 26.4892 | 30.4955 | 26.575 | 27.6165 | 27.4331 | 29.0125
255 | 24.0526 | 22.3249 | 24.04 | 22.5365 | 23.4368 | 20.5442 | 23.4817 | 24.2443 | 20.4739 | 17.4029 | 15.0048 | 14.4007 | 15.3103 | 14.9803 | 15.4567 | 15.9004 | 18.9813 | 20.5679 | 21.5031 | 21.5198 | 21.194 | 26.0945 | 25.6612 | 26.7651
256 | 25.9774 | 25.853 | 25.6219 | 25.6986 | 24.3368 | 21.0792 | 22.8219 | 21.6936 | 17.7859 | 12.8762 | 11.5336 | 11.118 | 11.7386 | 12.5889 | 16.8057 | 14.4879 | 14.4818 | 16.2179 | 19.9109 | 23.3328 | 24.3946 | 23.0059 | 23.8221 | 26.4081
257 | 24.5173 | 24.5767 | 25.5478 | 22.4223 | 21.0987 | 18.6759 | 19.2321 | 18.7394 | 16.5793 | 13.2828 | 12.6087 | 10.6262 | 12.8941 | 16.863 | 18.7537 | 22.1096 | 24.6829 | 25.9131 | 27.2082 | 33.7555 | 32.5768 | 32.6215 | 33.5955 | 31.7438
258 | 28.7579 | 30.8247 | 33.0417 | 31.8618 | 30.4538 | 24.5108 | 23.9991 | 21.8757 | 19.461 | 18.0236 | 16.608 | 15.8918 | 16.6396 | 16.6546 | 15.9147 | 18.5589 | 21.7229 | 25.6259 | 27.4891 | 27.2197 | 25.7472 | 25.7713 | 22.9951 | 23.2331
259 | 21.0902 | 22.1856 | 25.0276 | 26.191 | 27.3349 | 27.0201 | 27.9914 | 27.5381 | 23.8506 | 16.4166 | 12.2691 | 11.4191 | 14.3735 | 15.0748 | 16.6225 | 17.3304 | 20.5194 | 22.9184 | 25.8991 | 28.4257 | 24.8226 | 25.1463 | 24.6633 | 26.3988
260 | 26.7821 | 29.0905 | 33.992 | 31.1019 | 28.7906 | 27.8269 | 28.9299 | 29.5184 | 22.3682 | 13.9778 | 11.8244 | 14.8412 | 18.8237 | 20.3967 | 17.6647 | 21.1539 | 17.5262 | 19.5756 | 21.8467 | 26.4061 | 26.4589 | 28.7397 | 27.9568 | 28.7691
261 | 24.7881 | 23.7198 | 25.3275 | 25.4994 | 24.6318 | 23.5029 | 25.8911 | 25.4565 | 19.0183 | 10.5516 | 8.4444 | 10.0034 | 11.8522 | 14.4222 | 15.5557 | 15.8802 | 20.3778 | 24.5596 | 27.5805 | 27.6187 | 24.61 | 24.7393 | 28.7218 | 28.8726
262 | 27.4071 | 30.9137 | 32.4976 | 31.0166 | 30.3413 | 30.3446 | 29.262 | 26.8896 | 21.3034 | 13.1294 | 9.675 | 9.1223 | 11.927 | 12.06 | 12.2393 | 16.289 | 19.8807 | 20.7417 | 23.8692 | 27.3839 | 29.1246 | 33.2181 | 32.4447 | 30.9076
263 | 28.5079 | 30.6678 | 32.1344 | 32.0696 | 32.6526 | 28.7668 | 28.7979 | 24.4038 | 20.2513 | 14.1374 | 10.9472 | 11.6461 | 13.5578 | 16.1431 | 16.2934 | 15.4443 | 18.2378 | 21.7814 | 25.5503 | 24.5412 | 27.1385 | 25.6628 | 22.8526 | 24.7807
264 | 25.1806 | 27.1805 | 26.8485 | 26.749 | 26.2357 | 24.7284 | 24.5449 | 24.2795 | 20.9485 | 17.87 | 16.6957 | 15.5613 | 16.2453 | 18.9431 | 20.069 | 22.2216 | 21.5479 | 23.6336 | 28.9219 | 29.176 | 30.1231 | 30.7848 | 30.4742 | 29.6161
265 | 28.9531 | 29.0393 | 32.1807 | 29.3399 | 25.7462 | 19.2888 | 19.2418 | 17.0201 | 13.4651 | 10.047 | 12.3499 | 13.2355 | 14.5771 | 17.4729 | 18.7108 | 19.5927 | 24.5397 | 24.9331 | 25.4615 | 27.0685 | 23.9179 | 22.4058 | 25.8926 | 26.232
266 | 25.9264 | 24.6608 | 24.7478 | 26.5974 | 26.1736 | 24.5419 | 25.7181 | 26.4648 | 22.4327 | 19.3436 | 16.9226 | 18.3833 | 18.7972 | 18.8552 | 19.551 | 19.7482 | 23.0635 | 21.4775 | 25.7122 | 26.6131 | 21.8687 | 22.7072 | 23.4339 | 22.7385
267 | 21.0198 | 20.4798 | 24.4901 | 24.9903 | 22.7281 | 20.1892 | 20.0529 | 19.8986 | 15.7347 | 10.5186 | 10.1902 | 10.7801 | 12.5064 | 13.6018 | 12.965 | 14.3417 | 16.8079 | 16.7374 | 18.8782 | 19.246 | 19.6892 | 19.9723 | 21.0778 | 23.2199
268 | 23.7268 | 24.7506 | 26.5144 | 25.6253 | 22.807 | 22.2848 | 22.7112 | 22.0719 | 17.0639 | 12.8115 | 11.5042 | 11.06 | 10.6972 | 11.937 | 15.2878 | 17.7532 | 18.4484 | 18.1611 | 20.3199 | 24.0542 | 22.9061 | 23.3651 | 24.5825 | 25.5924
269 | 26.2603 | 28.4765 | 28.2423 | 27.0669 | 27.2416 | 26.3371 | 24.2054 | 21.8127 | 18.793 | 11.4464 | 7.3955 | 6.3989 | 8.05 | 9.1005 | 9.2659 | 11.7439 | 15.4066 | 17.3782 | 25.9003 | 28.6286 | 25.7075 | 26.6446 | 27.5372 | 26.0408
270 | 23.7247 | 21.7023 | 25.0997 | 26.988 | 28.2068 | 29.8036 | 29.4736 | 27.7199 | 18.9128 | 10.4788 | 8.6953 | 8.279 | 8.9563 | 10.4128 | 13.2217 | 14.0448 | 16.2346 | 16.6313 | 25.3589 | 27.5257 | 24.33 | 23.3732 | 27.8307 | 26.0542
271 | 25.327 | 25.5609 | 22.7145 | 21.3979 | 22.9094 | 21.5913 | 19.3203 | 16.343 | 12.7048 | 9.6952 | 10.51 | 10.7748 | 14.9391 | 15.9342 | 18.2249 | 20.5627 | 23.1168 | 23.6173 | 25.6815 | 24.4797 | 24.4563 | 22.4428 | 22.67 | 24.5269
272 | 23.5684 | 23.8121 | 22.5937 | 21.7984 | 24.3992 | 26.5194 | 25.636 | 23.6926 | 18.8812 | 15.048 | 14.2927 | 15.8002 | 16.9684 | 18.7392 | 17.6259 | 19.678 | 20.3119 | 21.6086 | 28.0622 | 30.722 | 29.8675 | 26.612 | 24.541 | 25.9248
273 | 25.8557 | 25.9135 | 25.1163 | 26.6739 | 25.4215 | 24.8058 | 23.0042 | 21.565 | 19.8281 | 15.8857 | 15.3793 | 16.3559 | 16.8219 | 15.819 | 13.8214 | 16.5974 | 16.73 | 17.9208 | 23.6798 | 25.998 | 23.4706 | 24.5255 | 22.094 | 23.1511
274 | 24.3609 | 27.2619 | 28.3926 | 29.6988 | 29.1129 | 26.4407 | 26.4027 | 23.4588 | 18.8738 | 13.3107 | 11.8555 | 12.9502 | 12.8354 | 11.4866 | 10.7424 | 14.7073 | 16.3868 | 17.4572 | 23.1856 | 26.4942 | 26.1568 | 25.2756 | 25.3147 | 24.9259
275 | 26.6213 | 28.8567 | 31.1578 | 30.6068 | 29.7545 | 29.3421 | 28.0109 | 27.6874 | 22.9397 | 17.5536 | 15.9203 | 13.334 | 15.082 | 13.9337 | 13.6532 | 14.7623 | 16.3866 | 17.5622 | 19.3765 | 26.0901 | 22.9253 | 23.8373 | 27.7376 | 32.3146
276 | 29.6073 | 27.5855 | 26.8648 | 25.7347 | 28.386 | 26.22 | 24.5881 | 23.7507 | 19.0234 | 15.1289 | 13.1452 | 12.3067 | 13.4753 | 14.5257 | 15.3155 | 21.3837 | 20.3203 | 22.9622 | 27.6075 | 30.6858 | 27.748 | 29.0541 | 27.0298 | 27.7631
277 | 26.9471 | 26.9785 | 25.7664 | 25.6234 | 25.9135 | 23.6813 | 23.3634 | 22.1585 | 17.9376 | 14.956 | 14.6907 | 15.2471 | 18.4069 | 20.8653 | 22.3206 | 25.5662 | 26.9599 | 24.8951 | 26.1901 | 27.1085 | 23.7718 | 23.1834 | 26.4687 | 29.1877
278 | 28.8595 | 28.2439 | 27.0605 | 26.8319 | 26.5615 | 26.53 | 20.7399 | 17.5513 | 14.4328 | 11.0425 | 10.9285 | 11.6866 | 14.1198 | 14.7628 | 16.4496 | 17.3769 | 20.4339 | 23.3798 | 26.0938 | 24.1805 | 23.6826 | 25.2202 | 23.3236 | 23.4373
279 | 23.0309 | 21.954 | 22.3518 | 23.8763 | 23.1254 | 22.8363 | 20.5208 | 20.5146 | 16.457 | 11.3798 | 12.2711 | 13.0372 | 16.2286 | 15.4313 | 15.9143 | 16.8242 | 19.7339 | 21.5181 | 22.8026 | 21.0193 | 23.2942 | 24.7373 | 28.1229 | 25.8247
280 | 23.9635 | 23.4832 | 23.1714 | 21.8259 | 22.8938 | 24.2603 | 24.0888 | 24.0264 | 20.1124 | 13.2026 | 11.9046 | 13.2406 | 16.6432 | 16.9975 | 17.0396 | 17.2012 | 17.3811 | 16.8467 | 19.8967 | 22.9174 | 22.4006 | 22.1746 | 24.6698 | 25.7726
281 | 26.585 | 30.4173 | 29.4422 | 28.5939 | 30.9351 | 31.5469 | 31.5702 | 28.835 | 19.8911 | 14.1825 | 13.2427 | 14.4762 | 15.1734 | 14.8801 | 14.1625 | 16.9045 | 14.3703 | 15.5298 | 20.3113 | 16.9266 | 16.9587 | 16.6548 | 17.5937 | 19.3788
282 | 20.2298 | 22.4972 | 21.4668 | 21.7845 | 20.6017 | 22.9399 | 21.733 | 19.373 | 14.7217 | 9.561 | 9.5717 | 11.6668 | 12.4944 | 13.3253 | 16.059 | 20.6106 | 20.2196 | 20.2056 | 23.4052 | 23.4061 | 23.3045 | 25.985 | 27.5237 | 28.6944
283 | 27.7133 | 27.2576 | 28.7422 | 30.6558 | 30.7137 | 31.1719 | 27.7624 | 23.4239 | 16.7966 | 11.116 | 10.2269 | 11.6328 | 13.3107 | 13.3868 | 14.4308 | 16.5682 | 19.0088 | 21.4352 | 23.3498 | 25.5258 | 27.4651 | 28.7056 | 31.4667 | 31.6759
284 | 33.2558 | 31.7134 | 30.0395 | 29.3729 | 29.5741 | 28.892 | 27.2713 | 25.4448 | 20.3203 | 15.4133 | 15.292 | 15.8772 | 19.6884 | 19.5226 | 20.2519 | 21.4131 | 23.0695 | 23.307 | 23.8826 | 23.9967 | 23.7166 | 28.0476 | 28.718 | 30.821
285 | 28.7079 | 28.3 | 27.9314 | 28.3841 | 27.9168 | 28.4432 | 27.6391 | 26.4163 | 21.8843 | 19.135 | 17.2541 | 15.8252 | 17.4226 | 16.6029 | 17.1592 | 16.2484 | 15.7047 | 17.3275 | 18.1655 | 17.2308 | 18.5377 | 21.7483 | 26.2203 | 29.0057
286 | 29.5826 | 28.5947 | 29.8703 | 30.7678 | 29.9346 | 32.329 | 30.4794 | 24.8591 | 17.751 | 13.742 | 11.5816 | 12.4202 | 12.7593 | 13.5505 | 14.5182 | 17.5535 | 18.4768 | 15.1919 | 20.4633 | 22.967 | 22.1881 | 22.526 | 24.2238 | 27.532
287 | 28.5205 | 29.8914 | 29.6952 | 30.6291 | 31.0984 | 29.8677 | 26.6415 | 24.1338 | 18.829 | 13.6535 | 13.0085 | 15.3176 | 19.1784 | 19.5557 | 18.5481 | 18.1696 | 18.7822 | 17.0432 | 20.5946 | 19.0834 | 19.8808 | 19.2144 | 24.0539 | 28.1307
288 | 28.6152 | 29.0129 | 28.6981 | 29.0737 | 28.7612 | 28.1762 | 26.0586 | 21.9814 | 17.42 | 14.4204 | 13.3231 | 15.9901 | 18.548 | 16.8232 | 16.7402 | 18.726 | 17.3216 | 18.2214 | 26.3421 | 25.2547 | 23.798 | 25.2007 | 27.7959 | 28.5132
289 | 29.8015 | 27.9578 | 26.1158 | 26.9249 | 27.8293 | 31.0096 | 31.1638 | 29.675 | 24.6599 | 21.9067 | 18.7572 | 17.9715 | 20.6338 | 21.0403 | 20.7255 | 22.2247 | 24.5774 | 25.2646 | 26.8618 | 26.5763 | 26.2586 | 27.8614 | 27.4683 | 31.4829
290 | 31.9514 | 32.1484 | 30.3257 | 29.9006 | 31.7413 | 32.598 | 29.3581 | 24.7574 | 20.8035 | 15.6857 | 14.5865 | 15.0897 | 17.3091 | 15.2883 | 16.1462 | 19.0178 | 18.785 | 16.4444 | 19.6546 | 20.4414 | 22.3337 | 24.4497 | 28.4626 | 28.0129
291 | 30.9044 | 30.4426 | 30.3893 | 28.7704 | 27.0755 | 26.8168 | 24.7111 | 23.814 | 20.8187 | 17.9963 | 15.1754 | 15.4366 | 17.7857 | 18.8113 | 19.4271 | 20.1061 | 18.6901 | 20.1365 | 21.8956 | 21.2418 | 18.9028 | 20.0667 | 22.7946 | 23.5033
292 | 25.8606 | 26.4177 | 27.9445 | 29.2656 | 30.2406 | 29.3566 | 26.1445 | 24.2891 | 21.2159 | 18.7354 | 16.5851 | 17.4821 | 17.6316 | 15.6664 | 14.4866 | 16.5166 | 15.8775 | 17.6128 | 19.1409 | 19.2648 | 18.6014 | 20.2444 | 23.6292 | 26.4957
293 | 26.4593 | 27.307 | 28.0882 | 29.59 | 30.6754 | 29.6233 | 28.164 | 23.7044 | 19.8261 | 14.5769 | 10.7546 | 11.6202 | 13.5134 | 13.0175 | 15.2758 | 15.9218 | 14.0361 | 18.0821 | 22.5759 | 21.5859 | 19.7859 | 21.6585 | 21.764 | 21.2869
294 | 24.9181 | 27.1318 | 25.0412 | 25.5232 | 27.3942 | 27.2724 | 24.3666 | 22.0115 | 20.7572 | 17.1585 | 14.6469 | 17.2048 | 20.5135 | 21.1197 | 22.5045 | 23.5371 | 22.2428 | 23.6137 | 24.8823 | 23.3842 | 21.517 | 23.4014 | 28.2179 | 27.9124
295 | 28.6832 | 28.2703 | 29.1264 | 30.6907 | 32.356 | 34.0044 | 32.3089 | 29.5593 | 26.3401 | 21.7415 | 18.9424 | 19.4745 | 18.772 | 17.5005 | 18.3552 | 20.8185 | 18.4656 | 20.5082 | 22.4915 | 20.7254 | 21.2776 | 23.2347 | 24.8383 | 28.1885
296 | 29.8818 | 30.3626 | 28.387 | 29.1359 | 30.5506 | 30.4601 | 27.05 | 25.0142 | 21.9999 | 16.9799 | 14.1738 | 14.3957 | 15.8245 | 16.2631 | 16.607 | 16.7838 | 16.4318 | 19.1014 | 21.3525 | 21.6352 | 23.6616 | 24.6483 | 26.8733 | 27.283
297 | 29.2166 | 31.2963 | 30.0298 | 28.9132 | 30.1524 | 29.9729 | 23.9097 | 19.9986 | 16.8601 | 14.5442 | 12.2941 | 12.0763 | 13.5339 | 13.087 | 13.8905 | 14.9133 | 16.0795 | 18.9214 | 20.8833 | 24.3831 | 25.1681 | 26.692 | 30.4927 | 29.2662
298 | 27.6216 | 28.3532 | 29.6829 | 27.7832 | 28.6028 | 29.7113 | 26.2888 | 23.1171 | 20.7944 | 18.0458 | 15.9989 | 16.6944 | 18.1316 | 17.678 | 16.0553 | 17.5364 | 18.7626 | 21.1196 | 24.8922 | 28.1892 | 28.2611 | 29.7702 | 30.9311 | 30.6969
299 | 31.8306 | 31.993 | 30.169 | 30.026 | 29.7641 | 29.2864 | 27.3408 | 27.2567 | 25.4395 | 20.8524 | 17.38 | 18.5747 | 20.1564 | 18.3848 | 17.6055 | 17.9586 | 14.0242 | 16.6108 | 18.2407 | 20.6265 | 20.0337 | 19.9165 | 21.5794 | 23.5399
300 | 27.6685 | 30.0469 | 28.9637 | 27.9699 | 28.5022 | 28.361 | 27.3302 | 25.9206 | 25.8663 | 22.7273 | 19.3366 | 17.1641 | 18.2202 | 18.254 | 19.8823 | 24.7337 | 25.5018 | 27.0643 | 27.8335 | 29.6009 | 28.8838 | 31.3201 | 29.9662 | 28.8023
301 | 26.2181 | 25.4659 | 25.1863 | 24.847 | 25.5136 | 25.1001 | 25.7422 | 25.6672 | 24.0495 | 19.7304 | 17.9778 | 19.6933 | 23.5193 | 23.3536 | 22.6239 | 23.6169 | 25.3471 | 24.2647 | 22.7339 | 27.3982 | 32.8265 | 33.7273 | 34.3653 | 33.1462
302 | 32.8047 | 33.5399 | 32.6924 | 33.1427 | 33.7348 | 31.6991 | 29.4294 | 28.5562 | 27.2399 | 24.7907 | 21.8296 | 22.3879 | 22.3014 | 22.5034 | 24.6726 | 27.9792 | 28.3413 | 31.0557 | 31.1385 | 31.8978 | 29.6382 | 30.7767 | 29.8275 | 32.0119
303 | 30.6838 | 29.8981 | 30.705 | 32.1905 | 32.4619 | 32.7114 | 31.3144 | 29.4939 | 25.5196 | 21.885 | 18.9857 | 18.3773 | 18.732 | 19.0916 | 17.3234 | 17.8623 | 20.48 | 21.6462 | 25.3502 | 27.2265 | 28.5274 | 26.7992 | 28.7974 | 26.4923
304 | 27.2096 | 29.552 | 28.4809 | 28.6952 | 31.14 | 31.5514 | 29.9107 | 28.7696 | 25.9584 | 20.8661 | 16.1648 | 16.0676 | 18.5303 | 19.7078 | 22.4176 | 22.5364 | 21.2692 | 22.6162 | 23.9291 | 26.8183 | 26.0391 | 30.3343 | 31.4779 | 33.2029
305 | 33.7523 | 35.993 | 33.8217 | 33.6353 | 33.7984 | 33.5821 | 30.1674 | 27.8268 | 25.5391 | 23.3428 | 23.1455 | 23.4903 | 22.9553 | 22.187 | 21.9377 | 20.4427 | 19.107 | 21.8363 | 22.8338 | 21.9486 | 21.7039 | 22.9429 | 24.1065 | 26.7774
306 | 28.2488 | 31.6832 | 32.629 | 33.148 | 32.4811 | 30.3429 | 27.6985 | 25.1804 | 22.3622 | 18.7883 | 15.0695 | 15.4799 | 18.5443 | 19.5403 | 19.4424 | 21.3263 | 20.0466 | 21.4831 | 21.0128 | 23.6201 | 24.7462 | 23.1413 | 23.5784 | 24.8272
307 | 25.6429 | 24.982 | 25.3066 | 26.4853 | 28.0991 | 28.215 | 26.6426 | 27.4079 | 27.1504 | 24.0271 | 20.7878 | 20.2921 | 22.1434 | 21.5339 | 20.3638 | 20.2223 | 19.46 | 21.6662 | 25.1015 | 26.1576 | 24.9077 | 26.5306 | 28.5747 | 27.3685
308 | 26.0151 | 25.4884 | 26.0731 | 26.8254 | 27.8349 | 24.9171 | 22.7675 | 22.5917 | 21.6745 | 17.2065 | 13.1314 | 12.2339 | 14.9976 | 16.2964 | 18.5317 | 21.9953 | 22.3238 | 24.0405 | 25.4031 | 26.2822 | 27.0664 | 28.0963 | 27.6147 | 29.6877
309 | 31.5042 | 32.5578 | 31.8277 | 31.9987 | 32.1015 | 32.4507 | 30.4371 | 29.366 | 27.8615 | 25.3204 | 20.2112 | 19.8621 | 21.3259 | 22.6141 | 21.9289 | 24.5815 | 23.6589 | 22.7169 | 24.4402 | 25.0898 | 25.8711 | 25.2782 | 24.8941 | 29.1334
310 | 29.6364 | 27.3593 | 27.6835 | 28.1104 | 29.716 | 31.4369 | 30.8609 | 31.5296 | 31.3686 | 30.0874 | 23.7349 | 20.431 | 19.4165 | 17.7385 | 16.2213 | 19.6284 | 19.21 | 23.1622 | 20.0628 | 21.2772 | 23.1098 | 30.5903 | 34.4618 | 34.5136
311 | 32.8044 | 33.1461 | 31.9326 | 32.3434 | 33.9577 | 34.5168 | 32.5614 | 32.8122 | 31.2421 | 28.521 | 23.1826 | 21.4375 | 22.2531 | 23.2013 | 23.4589 | 23.9089 | 22.8059 | 28.1714 | 30.3049 | 33.9466 | 31.6903 | 30.2907 | 31.7049 | 33.3639
312 | 33.7036 | 32.6774 | 31.2726 | 31.5661 | 31.9769 | 31.7007 | 29.3898 | 29.7413 | 28.887 | 28.9955 | 22.7989 | 21.16 | 22.6182 | 25.6195 | 27.6946 | 29.4293 | 27.5088 | 30.3079 | 31.1249 | 30.1786 | 28.6786 | 30.1688 | 28.7713 | 28.3386
313 | 28.4697 | 28.3426 | 27.8155 | 28.1967 | 27.6095 | 26.4218 | 26.6296 | 26.2592 | 24.4576 | 21.4173 | 17.1812 | 17.5726 | 18.6604 | 18.8017 | 21.2371 | 20.5013 | 18.4299 | 19.5168 | 23.1816 | 25.2079 | 26.5921 | 25.9282 | 25.1178 | 24.9467
314 | 26.366 | 27.15 | 25.782 | 25.1703 | 25.984 | 25.5518 | 25.0641 | 26.4441 | 26.3419 | 24.5157 | 18.9849 | 15.0313 | 16.4885 | 20.6627 | 21.1362 | 21.9797 | 20.9729 | 21.34 | 22.7899 | 26.7513 | 29.1848 | 26.9774 | 28.0456 | 28.7368
315 | 29.8727 | 31.0807 | 31.4233 | 32.3358 | 34.043 | 31.2587 | 29.4521 | 30.9329 | 31.1391 | 27.1867 | 19.2029 | 14.3891 | 13.3454 | 14.8423 | 17.2873 | 20.6254 | 20.4234 | 21.7605 | 21.4258 | 22.4528 | 26.5639 | 28.876 | 30.0313 | 30.4239
316 | 28.5302 | 29.0749 | 26.491 | 28.8267 | 29.5918 | 27.8729 | 24.4109 | 23.8957 | 24.1795 | 21.8007 | 18.022 | 15.365 | 16.7953 | 16.306 | 16.5463 | 17.677 | 19.1486 | 22.7252 | 21.061 | 26.2049 | 30.019 | 31.9569 | 33.1243 | 32.2263
317 | 31.1069 | 33.3506 | 34.6754 | 34.8642 | 33.6351 | 31.7056 | 29.066 | 30.5812 | 31.624 | 28.8498 | 25.7563 | 23.019 | 22.7928 | 23.6608 | 23.8287 | 24.8495 | 25.2923 | 27.5022 | 28.1428 | 29.5879 | 30.1452 | 30.1944 | 30.3204 | 31.7728
318 | 30.4385 | 29.7643 | 31.1997 | 29.4198 | 29.0029 | 29.6758 | 29.0974 | 30.8454 | 31.2231 | 27.6086 | 23.6027 | 21.1308 | 19.8889 | 22.0723 | 24.1698 | 25.8517 | 23.821 | 24.257 | 24.1684 | 27.3494 | 28.9087 | 28.8596 | 27.4304 | 26.6588
319 | 24.3312 | 27.2416 | 27.477 | 28.9182 | 27.4459 | 26.4635 | 25.3423 | 27.8821 | 26.4825 | 24.5152 | 21.4729 | 20.6266 | 22.836 | 23.6401 | 23.6427 | 23.9741 | 23.6997 | 22.6676 | 21.4271 | 23.6964 | 26.4127 | 28.8615 | 27.8696 | 27.9331
320 | 27.0974 | 29.2626 | 29.655 | 30.371 | 30.1694 | 29.8138 | 28.6249 | 28.7606 | 27.3893 | 25.4281 | 18.284 | 14.2166 | 17.2216 | 19.0422 | 20.1519 | 21.1754 | 20.6804 | 24.0495 | 26.789 | 29.0211 | 27.6968 | 29.5768 | 32.7863 | 32.9167
321 | 31.1513 | 31.6904 | 30.9602 | 32.4731 | 32.4489 | 29.9566 | 28.5944 | 29.8119 | 28.8859 | 26.731 | 23.1731 | 21.0431 | 21.2434 | 20.7029 | 20.1651 | 21.9095 | 19.1996 | 21.7648 | 28.9381 | 33.6696 | 35.563 | 35.0101 | 35.4233 | 35.3862
322 | 35.5939 | 36.6177 | 36.3905 | 36.8646 | 35.8559 | 33.5042 | 30.4027 | 30.7387 | 32.1773 | 29.2682 | 23.7102 | 20.7259 | 21.4951 | 23.0178 | 24.2848 | 27.5223 | 27.7459 | 27.5501 | 27.9411 | 29.1476 | 32.2188 | 35.0912 | 33.8941 | 35.0808
323 | 36.0428 | 34.9591 | 31.6414 | 32.0053 | 29.5823 | 25.8893 | 23.4937 | 23.6873 | 23.8588 | 22.1125 | 18.6728 | 17.9839 | 20.1542 | 19.858 | 18.951 | 19.8046 | 19.8986 | 22.0992 | 22.3899 | 23.9823 | 24.2351 | 25.4698 | 27.6711 | 27.8247
324 | 27.5419 | 29.306 | 30.1708 | 31.4746 | 31.6884 | 32.0692 | 29.759 | 29.0544 | 30.3645 | 28.8654 | 21.1278 | 17.8724 | 17.4081 | 17.7172 | 16.8807 | 18.4242 | 18.5698 | 22.3795 | 21.762 | 24.8728 | 27.1798 | 30.0275 | 30.5655 | 32.6922
325 | 34.224 | 36.8606 | 35.5324 | 35.7876 | 34.1967 | 33.6831 | 31.1973 | 33.2144 | 32.9249 | 29.5251 | 25.1286 | 22.0343 | 24.5799 | 25.0952 | 27.4401 | 27.0164 | 26.4548 | 26.8806 | 27.7425 | 27.244 | 29.8119 | 32.725 | 34.3831 | 35.1265
326 | 33.2023 | 32.158 | 31.2451 | 33.4861 | 34.7723 | 34.5629 | 32.9736 | 34.0462 | 33.6591 | 30.3768 | 26.9962 | 25.7896 | 26.4593 | 23.4986 | 21.1875 | 22.0127 | 21.829 | 22.3011 | 23.9324 | 23.1025 | 27.0053 | 28.5247 | 28.1676 | 26.5668
327 | 26.5791 | 27.3347 | 25.9539 | 26.2962 | 28.7 | 28.432 | 25.7359 | 25.6633 | 26.1943 | 23.2498 | 19.6998 | 18.3827 | 18.195 | 19.7023 | 18.96 | 19.5828 | 20.5696 | 22.2967 | 21.8739 | 26.0918 | 31.0582 | 31.605 | 32.132 | 32.7625
328 | 34.6418 | 37.4762 | 37.2138 | 36.4448 | 36.0196 | 34.0645 | 31.2002 | 31.7699 | 31.8751 | 29.5585 | 27.3397 | 23.8702 | 26.4605 | 27.5294 | 26.7148 | 25.5762 | 25.2598 | 25.7317 | 25.3356 | 24.4354 | 23.5852 | 24.1858 | 28.6558 | 34.3401
329 | 37.2317 | 38.6895 | 39.2127 | 38.8343 | 36.8067 | 35.8682 | 36.3954 | 34.6419 | 31.1893 | 29.8186 | 24.2721 | 21.8454 | 20.4482 | 22.5469 | 22.605 | 23.621 | 23.9515 | 23.5137 | 28.0405 | 30.3705 | 32.0032 | 31.6 | 30.5542 | 30.6672
330 | 32.0339 | 34.1226 | 31.7314 | 30.7394 | 30.5463 | 27.9789 | 26.6333 | 26.2488 | 26.1497 | 26.0318 | 22.969 | 22.6722 | 25.8984 | 27.2699 | 27.2554 | 26.6168 | 24.1959 | 23.3179 | 24.2489 | 24.1785 | 26.971 | 29.303 | 27.6327 | 25.964
331 | 26.658 | 27.489 | 25.8958 | 26.3882 | 26.7092 | 26.5017 | 26.8142 | 26.4605 | 27.3537 | 26.3872 | 23.0065 | 19.7679 | 19.0837 | 20.5409 | 18.9157 | 20.7113 | 21.0348 | 22.5212 | 22.8792 | 25.0291 | 27.5269 | 28.0574 | 30.9364 | 32.4859
332 | 36.8903 | 38.3137 | 37.8202 | 38.8823 | 39.7245 | 37.8844 | 35.4014 | 32.4109 | 30.9007 | 27.0932 | 22.8539 | 20.3537 | 21.0582 | 22.2791 | 22.0781 | 23.1443 | 24.3487 | 25.3678 | 21.9235 | 22.3484 | 24.4351 | 24.2445 | 26.4813 | 28.3881
333 | 27.8085 | 28.4896 | 28.8091 | 30.9629 | 33.7254 | 33.4233 | 30.9918 | 31.6152 | 31.7939 | 31.0455 | 26.8155 | 24.0841 | 25.4928 | 28.1586 | 24.2376 | 25.4153 | 24.8464 | 24.8296 | 25.2051 | 24.8607 | 25.9088 | 28.9603 | 28.6497 | 29.3391
334 | 30.2411 | 31.6492 | 32.9358 | 33.6324 | 34.0457 | 33.5294 | 33.2951 | 32.214 | 31.5961 | 29.8386 | 26.6528 | 25.68 | 26.4112 | 25.2763 | 24.962 | 24.8451 | 27.4851 | 31.4689 | 33.0759 | 33.4182 | 33.4774 | 30.9122 | 30.3698 | 29.5672
335 | 30.7654 | 32.9805 | 34.2909 | 36.9232 | 37.0823 | 35.5344 | 34.3369 | 33.0689 | 33.163 | 32.1537 | 26.8331 | 24.7757 | 23.763 | 23.6964 | 25.6466 | 27.423 | 28.268 | 28.3819 | 27.254 | 30.0145 | 29.9324 | 29.9426 | 31.6465 | 34.9792
336 | 34.374 | 34.0275 | 33.5825 | 35.7595 | 37.3561 | 37.5865 | 36.3848 | 35.9288 | 33.8482 | 31.6922 | 29.5511 | 26.1946 | 29.5074 | 28.3852 | 27.4512 | 25.907 | 26.8444 | 28.0619 | 29.8002 | 30.3727 | 32.0726 | 30.8326 | 31.1891 | 28.8726
337 | 27.7435 | 30.2793 | 28.6957 | 29.1349 | 31.8819 | 31.4402 | 29.8087 | 29.2571 | 28.9986 | 27.3659 | 22.4623 | 18.8115 | 17.9943 | 18.1236 | 18.1938 | 17.2821 | 18.2399 | 19.2703 | 19.8943 | 21.2449 | 25.9279 | 25.6856 | 28.5135 | 29.1571
338 | 26.8128 | 27.8241 | 29.0524 | 29.0036 | 30.7644 | 30.3413 | 27.742 | 26.4338 | 25.6511 | 22.7085 | 19.8106 | 18.4215 | 18.7866 | 20.0037 | 20.034 | 20.1983 | 19.4039 | 21.4826 | 21.9297 | 25.6873 | 28.9212 | 27.9493 | 30.3107 | 32.048
339 | 31.3383 | 32.4336 | 31.9121 | 33.2456 | 34.7518 | 35.013 | 33.5532 | 32.9951 | 32.4248 | 30.4749 | 24.7275 | 21.5444 | 22.3446 | 22.1985 | 21.3373 | 20.6871 | 21.4227 | 24.8287 | 23.6378 | 22.9545 | 26.5948 | 28.6305 | 29.5727 | 29.5779
340 | 27.9626 | 27.7294 | 27.1845 | 29.6284 | 32.164 | 32.1536 | 30.7812 | 27.7262 | 27.347 | 25.9863 | 21.3413 | 15.6138 | 16.8861 | 17.5486 | 16.8809 | 18.002 | 21.9538 | 24.1891 | 21.2983 | 22.6599 | 27.5582 | 30.395 | 31.9802 | 34.1252
341 | 34.9829 | 35.7582 | 35.1645 | 35.1943 | 35.1729 | 33.6832 | 31.7764 | 33.3914 | 34.3232 | 32.4122 | 27.7829 | 21.2442 | 20.192 | 20.8343 | 23.0483 | 24.165 | 22.5 | 23.309 | 22.1993 | 22.7605 | 25.6812 | 26.0898 | 28.2238 | 27.7502
342 | 26.0632 | 26.5831 | 26.8701 | 29.0504 | 31.6381 | 32.8466 | 33.2847 | 33.2387 | 33.5413 | 30.2784 | 25.7792 | 20.3993 | 19.0328 | 18.1795 | 18.1909 | 19.0246 | 22.1648 | 24.3769 | 24.9791 | 22.5626 | 25.1396 | 25.6833 | 28.3285 | 28.0258
343 | 26.2623 | 29.2047 | 31.0717 | 30.9862 | 34.0407 | 34.2377 | 33.7074 | 31.772 | 31.009 | 29.3441 | 26.2696 | 24.6838 | 26.0136 | 25.0079 | 24.1617 | 22.7026 | 22.2496 | 24.4667 | 25.8447 | 27.66 | 30.266 | 29.7753 | 29.6046 | 30.623
344 | 32.706 | 34.1058 | 34.8902 | 37.2094 | 38.5222 | 36.6443 | 34.4006 | 31.2391 | 30.4424 | 29.1545 | 23.3962 | 17.9229 | 19.2414 | 19.7442 | 20.9203 | 19.0119 | 21.1397 | 23.4712 | 25.1355 | 26.444 | 28.4857 | 28.3083 | 29.1364 | 29.7694
345 | 31.2333 | 33.0945 | 32.4792 | 33.0512 | 34.1012 | 33.5931 | 33.8298 | 32.9986 | 33.6443 | 30.1088 | 26.3785 | 20.3818 | 19.654 | 19.7233 | 19.4607 | 20.4472 | 22.4609 | 21.804 | 22.8618 | 23.441 | 26.2479 | 26.525 | 29.414 | 33.707
346 | 34.8412 | 35.683 | 34.2706 | 33.8723 | 35.2482 | 33.2562 | 29.5338 | 28.3845 | 27.5025 | 24.9154 | 20.9431 | 19.4274 | 20.6022 | 20.932 | 20.0192 | 19.7921 | 21.1143 | 22.2294 | 23.2816 | 21.7746 | 24.5133 | 24.6361 | 27.3972 | 31.004
347 | 33.8876 | 37.5491 | 37.5749 | 37.6368 | 41.1402 | 38.2817 | 37.0624 | 35.034 | 33.546 | 30.2539 | 26.8024 | 24.3919 | 24.7498 | 23.9392 | 23.7693 | 23.1612 | 25.7766 | 29.0707 | 30.3639 | 31.2128 | 31.6648 | 33.3794 | 35.281 | 35.063
348 | 35.5621 | 35.6232 | 33.4357 | 34.471 | 34.8288 | 35.2572 | 34.0767 | 31.6765 | 32.4892 | 30.6527 | 26.3501 | 22.7612 | 23.6402 | 24.0849 | 23.0429 | 23.18 | 25.2771 | 28.4402 | 32.5496 | 32.0338 | 33.7968 | 34.276 | 35.9903 | 35.1203
349 | 33.4842 | 34.6119 | 34.8703 | 36.5198 | 35.5528 | 34.5418 | 32.8059 | 31.9373 | 31.115 | 28.8198 | 23.7958 | 22.8898 | 25.1847 | 26.2197 | 26.1211 | 24.499 | 22.6918 | 25.3861 | 30.1814 | 30.0998 | 30.0269 | 28.0392 | 29.8222 | 28.7669
350 | 31.2983 | 34.5594 | 36.895 | 39.8162 | 39.955 | 38.6945 | 36.9413 | 33.725 | 30.7846 | 27.4382 | 20.4058 | 17.4131 | 17.2549 | 17.7563 | 18.2894 | 17.8276 | 20.8125 | 24.0656 | 28.9046 | 28.604 | 28.7262 | 27.54 | 29.0681 | 29.8095
351 | 30.2661 | 32.4793 | 33.1399 | 34.816 | 35.0239 | 31.385 | 28.859 | 26.876 | 26.7138 | 25.7867 | 23.4144 | 20.7537 | 21.4501 | 21.9289 | 23.17 | 23.281 | 23.0803 | 22.1667 | 21.5482 | 22.1616 | 23.6743 | 22.5312 | 26.4107 | 25.7705
352 | 25.027 | 26.4496 | 28.0847 | 30.7088 | 32.0131 | 33.5117 | 35.1008 | 36.0305 | 35.5784 | 34.3044 | 27.7091 | 25.1933 | 25.2796 | 23.3236 | 22.0641 | 19.9717 | 21.9932 | 25.2199 | 25.6809 | 24.3974 | 26.5762 | 26.8353 | 27.7526 | 29.6443
353 | 30.042 | 29.8016 | 28.6987 | 30.582 | 31.8886 | 32.3111 | 33.1446 | 32.7475 | 31.0899 | 28.8588 | 24.5484 | 21.2636 | 20.4235 | 21.0166 | 22.474 | 23.7677 | 25.7753 | 27.1279 | 28.1064 | 26.8925 | 29.7231 | 30.5405 | 31.1471 | 30.9181
354 | 31.9716 | 33.2918 | 33.0208 | 32.9552 | 33.8696 | 32.8416 | 30.4702 | 29.3947 | 30.2852 | 27.8796 | 21.5224 | 18.6461 | 20.6651 | 22.9589 | 23.7019 | 24.7055 | 24.7814 | 23.719 | 23.9583 | 24.0503 | 26.127 | 27.3632 | 29.3532 | 31.7112
355 | 32.9867 | 33.8648 | 33.5395 | 32.6789 | 31.8756 | 31.8695 | 31.1494 | 29.0157 | 27.5728 | 25.6826 | 21.1913 | 17.3889 | 17.7719 | 19.5088 | 21.1274 | 22.4341 | 23.1691 | 24.2449 | 27.2382 | 24.8744 | 25.9589 | 25.2421 | 29.0864 | 29.7356
356 | 30.8276 | 32.5657 | 32.8445 | 31.3886 | 31.6384 | 31.4367 | 28.1019 | 24.5004 | 27.3984 | 27.1562 | 24.0955 | 22.1317 | 22.5677 | 23.0019 | 24.8773 | 26.2745 | 27.1841 | 28.4222 | 28.8736 | 26.1077 | 27.4237 | 28.0101 | 29.4963 | 28.5265
357 | 30.1276 | 29.9767 | 28.9204 | 31.1205 | 32.7744 | 32.0009 | 28.5842 | 27.005 | 26.9083 | 24.5847 | 22.1942 | 21.2231 | 22.6781 | 23.5538 | 22.2805 | 22.1747 | 19.8759 | 22.3406 | 20.6974 | 17.9994 | 19.6771 | 20.3153 | 23.4085 | 25.6652
358 | 28.9416 | 31.4387 | 29.8748 | 33.1977 | 35.7217 | 34.6214 | 32.6622 | 29.7332 | 24.8247 | 23.326 | 19.6086 | 15.3926 | 16.9849 | 16.1838 | 15.1401 | 16.4427 | 17.8307 | 22.9103 | 25.8944 | 25.8219 | 25.9406 | 24.6297 | 25.883 | 26.8995
359 | 27.5175 | 27.5108 | 29.8696 | 32.7841 | 34.8598 | 33.5482 | 32.9278 | 29.8253 | 27.6317 | 26.3429 | 21.854 | 18.5795 | 18.9276 | 18.3509 | 18.1721 | 18.4783 | 20.5234 | 23.6208 | 24.8104 | 24.426 | 25.3297 | 26.2897 | 28.3301 | 29.2399
360 | 29.8851 | 31.4359 | 32.0785 | 34.9598 | 37.0621 | 36.1619 | 35.3349 | 36.0073 | 35.3194 | 33.4623 | 27.6759 | 22.3404 | 22.3129 | 21.8503 | 21.4078 | 22.4756 | 22.1794 | 25.0887 | 24.119 | 21.7319 | 22.0409 | 25.2948 | 28.5816 | 31.266
361 | 32.2308 | 34.0218 | 34.3777 | 34.2324 | 33.8113 | 32.9356 | 31.3975 | 29.8447 | 28.2046 | 27.325 | 25.2909 | 23.9637 | 23.7283 | 21.1798 | 21.7528 | 21.4371 | 22.7577 | 27.2356 | 30.5711 | 29.6843 | 30.4292 | 31.0251 | 32.5318 | 31.9157
362 | 32.0214 | 31.9734 | 33.7505 | 35.0189 | 35.6193 | 35.2791 | 34.0709 | 32.727 | 33.3018 | 32.416 | 26.083 | 20.2258 | 19.4148 | 18.0015 | 16.8307 | 18.1036 | 20.8869 | 25.1099 | 26.7268 | 24.9186 | 24.9384 | 22.9326 | 24.909 | 26.786
363 | 28.8616 | 30.3659 | 29.8118 | 32.0258 | 33.8981 | 32.9366 | 32.5708 | 31.1205 | 30.887 | 28.2832 | 25.7221 | 21.7543 | 21.627 | 21.6513 | 20.213 | 22.1668 | 23.0898 | 27.8415 | 29.1387 | 27.3034 | 28.3644 | 30.7398 | 34.8906 | 36.4114
364 | 37.7552 | 39.9267 | 38.943 | 41.0538 | 43.1303 | 41.5325 | 38.6366 | 36.6972 | 33.7597 | 31.4301 | 29.0191 | 25.4757 | 25.8035 | 24.9261 | 24.9336 | 25.6774 | 26.7344 | 29.0772 | 30.7776 | 26.9115 | 24.6127 | 25.6202 | 26.8582 | 26.8372
365 | 29.239 | 30.0942 | 29.3208 | 26.1093 | 27.5318 | 27.6003 | 27.3856 | 26.4774 | 25.1668 | 24.1129 | 22.3556 | 20.879 | 19.1782 | 17.6272 | 17.1587 | 20.2233 | 23.3821 | 29.1223 | 30.3257 | 29.6685 | 29.0669 | 28.0668 | 29.9822 | 31.8142
8760 - Energy Profile
version 1-1
CLIENT: BLACK HILLS CORP.
PROJECT: LA CUMBRE
TURBINE: GE2.5-127 and GE2.3-116
HUB HEIGHT: 80M and 89M
ALL DATA PRESENTED IN THIS PRELIMINARY REPORT ARE DRAFT AND ARE SUBJECT TO CHANGE DURING THE FINAL QUALITY CONTROL PROCESS.

## 8760-TMY
Date are in local time (UTC -7)
Values represent a "typical meterological year" in that the sum if the year is equal to the annual P50, but the hour to hour variability is more realistic.
MWh | HOUR
DAY | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
1 | 28.4726 | 28.0936 | 28.7629 | 37.2247 | 47.9217 | 49.8533 | 47.1325 | 36.136 | 17.2727 | 4.4885 | 1.3513 | 6.3494 | 5.2381 | 4.627 | 6.5547 | 5.6898 | 6.6275 | 12.3887 | 12.8516 | 9.1341 | 10.4583 | 15.8398 | 18.9509 | 15.6603
2 | 11.4163 | 7.5963 | 7.4743 | 9.8128 | 10.0245 | 9.2996 | 7.6218 | 5.1011 | 4.3486 | 2.5137 | 0.33771 | 0 | 0 | 0 | 0 | 0.26807 | 2.6248 | 3.3032 | 9.357 | 39.2931 | 58.1535 | 59.6 | 59.6 | 59.6
3 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 59.5981 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6
4 | 59.6 | 59.6 | 59.6 | 59.4734 | 58.047 | 58.119 | 58.8361 | 59.5813 | 59.6 | 55.7911 | 33.9071 | 55.0553 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 50.3555 | 36.0577 | 53.5127 | 59.567 | 59.6 | 57.7797
5 | 57.1562 | 59.6 | 57.5945 | 11.2256 | 18.0232 | 28.5606 | 56.7692 | 59.6 | 57.4512 | 30.6394 | 3.6047 | 4.8062 | 18.4237 | 23.121 | 27.2244 | 41.0862 | 47.8161 | 36.9755 | 27.7095 | 24.5137 | 34.6512 | 40.8679 | 47.2817 | 53.4412
6 | 56.9537 | 39.1504 | 15.8204 | 8.4109 | 1.2015 | 6.0077 | 27.7357 | 58.6531 | 39.5099 | 6.7593 | 20.1063 | 59.5143 | 59.6 | 59.6 | 59.6 | 59.6 | 50.619 | 16.3022 | 20.4389 | 17.6102 | 19.8694 | 16.2913 | 20.447 | 29.5944
7 | 26.1905 | 16.9873 | 19.5828 | 36.9718 | 52.6344 | 59.6 | 59.6 | 59.6 | 59.6 | 58.5204 | 18.844 | 0.040043 | 1.5799 | 16.6078 | 12.468 | 53.3863 | 59.6 | 59.5074 | 54.2029 | 59.6 | 46.2435 | 31.7865 | 28.6038 | 11.9649
8 | 0 | 0.040043 | 0 | 0 | 0.81871 | 5.5096 | 10.0218 | 10.8982 | 9.1346 | 14.3714 | 19.1841 | 16.4672 | 19.6601 | 13.4425 | 9.1423 | 10.4745 | 11.7387 | 29.1397 | 50.2001 | 21.4866 | 48.927 | 59.6 | 59.6 | 59.6
9 | 59.6 | 59.6 | 53.468 | 28.2401 | 20.4264 | 13.6264 | 10.5845 | 16.8774 | 19.5424 | 21.4311 | 13.2064 | 11.1585 | 3.0043 | 0.79507 | 0.40007 | 2.1943 | 6.8973 | 20.3129 | 31.9514 | 21.3731 | 15.8493 | 15.0369 | 16.3315 | 16.4258
10 | 16.6498 | 9.8852 | 1.5423 | 8.9337 | 17.7503 | 17.1993 | 22.9893 | 24.9299 | 24.6275 | 30.4007 | 27.443 | 17.0849 | 17.5603 | 24.8152 | 20.3988 | 21.7888 | 19.2773 | 15.4781 | 6.2825 | 1.2523 | 3.4481 | 8.2559 | 10.1177 | 7.2621
11 | 7.7825 | 5.0438 | 1.1325 | 0 | 0.44423 | 4.3614 | 6.7146 | 10.5139 | 11.246 | 11.0755 | 11.0177 | 11.4656 | 17.0491 | 15.1637 | 12.1567 | 11.8682 | 12.7095 | 20.7236 | 25.8657 | 11.9356 | 2.4607 | 0 | 0 | 0
12 | 1.7081 | 5.4768 | 9.8492 | 16.7143 | 31.9921 | 37.1312 | 36.208 | 32.5669 | 28.9442 | 21.0486 | 9.5839 | 3.6729 | 0.9596 | 1.3537 | 6.4994 | 18.8173 | 48.6635 | 59.6 | 59.6 | 59.2578 | 58.6048 | 59.4132 | 59.6 | 59.6
13 | 59.6 | 55.073 | 53.8003 | 49.1634 | 44.4209 | 29.5178 | 14.5148 | 8.856 | 7.97 | 9.0803 | 13.4005 | 4.9168 | 25.3781 | 33.1759 | 34.6986 | 40.1461 | 28.293 | 28.2432 | 48.3587 | 59.6 | 51.4021 | 19.5066 | 12.4716 | 12.8158
14 | 13.7198 | 12.9441 | 15.4189 | 6.0423 | 1.4117 | 1.8912 | 6.6598 | 10.9005 | 5.4462 | 3.9184 | 9.2758 | 10.192 | 3.7716 | 2.4521 | 3.7416 | 7.2671 | 9.2467 | 15.7463 | 13.4702 | 8.6044 | 3.652 | 1.1728 | 0.33592 | 0.12013
15 | 0.040043 | 0 | 0.080086 | 1.9362 | 2.9044 | 2.2438 | 6.9613 | 8.1439 | 11.4781 | 15.383 | 13.5434 | 6.3115 | 4.7485 | 7.5958 | 5.721 | 6.3565 | 3.2138 | 6.1998 | 3.9612 | 0.39088 | 0.85976 | 2.303 | 11.7177 | 18.2491
16 | 33.8519 | 40.6837 | 35.3681 | 21.5622 | 15.4753 | 14.6166 | 16.6554 | 21.0271 | 28.0125 | 47.6783 | 47.7803 | 19.2396 | 9.287 | 1.4512 | 0.040043 | 0 | 0 | 0.040043 | 2.0707 | 4.3619 | 4.7118 | 34.653 | 57.2581 | 55.0547
17 | 51.811 | 56.5125 | 52.5645 | 51.6259 | 51.2697 | 34.7442 | 22.5998 | 27.5576 | 23.2868 | 16.4832 | 12.7776 | 7.1548 | 0.28036 | 0 | 0.83207 | 4.4818 | 1.799 | 0.36039 | 0.080086 | 0.40049 | 0 | 0.43588 | 11.1727 | 42.1032
18 | 59.5443 | 59.6 | 59.5886 | 59.6 | 59.6 | 59.6 | 59.5598 | 59.6 | 59.6 | 57.7789 | 32.8802 | 20.6529 | 21.4003 | 18.0932 | 28.3699 | 58.9652 | 59.6 | 59.6 | 59.6 | 58.6054 | 52.0358 | 59.3407 | 59.6 | 59.6
19 | 59.6 | 46.1728 | 46.6865 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 59.5702 | 59.6 | 59.6 | 59.6 | 55.7937 | 32.1101 | 43.9961 | 58.0891
20 | 59.6 | 59.6 | 19.8343 | 13.3227 | 8.4 | 10.2377 | 14.9277 | 32.1865 | 50.0237 | 46.5371 | 14.6963 | 11.4868 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 58.8465 | 59.2872 | 59.4099 | 59.6
21 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 57.8171 | 57.7336 | 59.2633 | 46.7716 | 10.3844 | 0 | 12.0798 | 38.1033 | 49.0188 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 59.1377 | 58.0529 | 59.6 | 59.6
22 | 35.5023 | 43.0671 | 18.2103 | 9.9197 | 2.3149 | 0.5729 | 0 | 0.5535 | 1.9501 | 5.1228 | 8.8898 | 13.6052 | 21.6593 | 25.8609 | 29.9637 | 37.8392 | 35.3238 | 33.8057 | 19.14 | 7.2494 | 18.7171 | 22.922 | 17.0975 | 28.8685
23 | 55.5657 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 56.634 | 36.9707 | 21.2564 | 6.0176 | 1.07 | 0.080086 | 0 | 0 | 1.5348 | 6.6625 | 6.6733 | 8.1502 | 7.4921 | 10.9982
24 | 22.4375 | 31.1061 | 32.356 | 38.0187 | 39.6926 | 43.6903 | 44.6771 | 42.9992 | 33.1622 | 28.6208 | 25.8569 | 11.012 | 0 | 0 | 0 | 0.080922 | 0.12013 | 1.708 | 0 | 20.6451 | 56.5816 | 58.73 | 59.6 | 59.6
25 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 59.5232 | 41.5899 | 27.5397 | 18.2565 | 16.1129 | 18.1127 | 17.7119 | 15.5682 | 14.622 | 27.3187 | 9.6463 | 0.49168 | 0.61545 | 0.42818 | 0.13391
26 | 0.30662 | 1.1163 | 2.1898 | 0.7724 | 1.4882 | 3.037 | 7.6966 | 11.1238 | 11.2388 | 18.8659 | 25.9944 | 10.9489 | 2.2894 | 0.46035 | 1.4682 | 10.1805 | 34.517 | 22.5801 | 44.0765 | 37.3036 | 39.8617 | 33.9054 | 49.9556 | 57.9418
27 | 53.4732 | 53.5527 | 57.7999 | 58.3694 | 59.529 | 59.6 | 59.6 | 59.6 | 59.3433 | 58.0982 | 59.5089 | 59.5476 | 58.8912 | 56.0733 | 59.4241 | 59.6 | 58.1914 | 53.1293 | 58.832 | 43.1554 | 18.4287 | 24.7385 | 28.4855 | 16.3895
28 | 4.1675 | 14.8821 | 55.9378 | 59.6 | 59.6 | 59.6 | 45.0661 | 29.6995 | 47.5069 | 57.4453 | 59.0023 | 56.7834 | 58.8932 | 57.1142 | 51.6516 | 40.1945 | 10.1039 | 4.5261 | 0.58394 | 0.22027 | 0 | 0 | 0 | 1.58
29 | 9.938 | 11.7753 | 6.9316 | 3.5885 | 3.1468 | 3.6278 | 3.2347 | 3.302 | 2.6872 | 0.45933 | 0 | 5.8708 | 20.3089 | 36.5005 | 45.37 | 59.0685 | 56.2345 | 50.4158 | 41.2 | 36.3256 | 12.9081 | 30.2445 | 41.369 | 42.802
30 | 44.9366 | 31.9012 | 31.802 | 29.1471 | 33.9245 | 30.6854 | 33.8741 | 28.463 | 26.5268 | 29.0131 | 32.1517 | 29.8533 | 37.6188 | 35.7835 | 16.0901 | 17.722 | 14.6767 | 5.6479 | 1.1653 | 0 | 0 | 2.6892 | 11.286 | 15.3208
31 | 17.7186 | 21.4761 | 16.5048 | 13.2324 | 14.3577 | 11.6395 | 13.2013 | 15.5752 | 11.808 | 7.0095 | 4.1062 | 9.1247 | 15.5919 | 13.647 | 7.2993 | 4 | 3.5951 | 5.4358 | 4.6865 | 1.3504 | 0.40938 | 3.2714 | 4.3433 | 8.7164
32 | 10.5904 | 14.5219 | 18.5535 | 14.441 | 11.96 | 6.9714 | 3.6621 | 3.6578 | 4.2772 | 4.4666 | 9.5649 | 16.3879 | 21.5491 | 24.4992 | 34.5541 | 35.7434 | 39.6432 | 24.6381 | 19.4721 | 19.0413 | 9.1298 | 6.3444 | 5.2738 | 5.3824
33 | 5.42 | 3.7888 | 1.4846 | 1.507 | 3.86 | 7.1323 | 12.5286 | 15.8932 | 11.312 | 8.7037 | 4.3477 | 4.6811 | 3.0976 | 4.4807 | 9.1238 | 15.3835 | 31.9988 | 26.6463 | 25.7123 | 22.9122 | 7.5579 | 0.81823 | 6.3418 | 7.9495
34 | 6.8329 | 6.8964 | 3.389 | 4.2374 | 5.0504 | 6.663 | 10.2028 | 19.2029 | 28.7919 | 32.2394 | 12.4301 | 3.6119 | 1.9561 | 3.6599 | 4.8641 | 40.868 | 47.3049 | 33.6421 | 5.2399 | 6.7687 | 4.4425 | 12.3527 | 16.0426 | 7.0006
35 | 2.3982 | 14.7133 | 13.0957 | 20.4288 | 9.0451 | 9.2183 | 15.8867 | 16.7386 | 11.2671 | 8.5416 | 10.7544 | 14.3566 | 25.6484 | 18.8138 | 15.0978 | 30.285 | 33.6937 | 33.9449 | 41.8252 | 34.4915 | 29.9268 | 30.567 | 35.6987 | 39.0153
36 | 54.8804 | 50.6151 | 44.9309 | 28.5318 | 16.4933 | 12.451 | 10.8217 | 11.3903 | 14.172 | 16.9596 | 22.4837 | 31.9735 | 35.4433 | 32.5747 | 34.2094 | 51.119 | 54.3038 | 54.5098 | 53.5485 | 42.9006 | 24.7991 | 17.386 | 14.1074 | 14.0292
37 | 10.8129 | 6.5412 | 5.8914 | 4.6391 | 2.915 | 1.1909 | 0.29671 | 0.86848 | 2.7122 | 10.5131 | 20.1148 | 23.3671 | 19.1326 | 15.1898 | 15.1133 | 24.0135 | 33.628 | 22.282 | 14.092 | 10.2501 | 10.3756 | 14.7057 | 21.0064 | 29.1724
38 | 22.1002 | 23.9748 | 38.333 | 57.9301 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 59.0231 | 51.1636 | 58.1069 | 59.2686 | 58.3906 | 58.9359 | 58.289 | 53.6625 | 53.1922 | 57.7664 | 59.6
39 | 59.6 | 58.7953 | 58.8526 | 59.0888 | 55.9099 | 45.2575 | 32.4242 | 30.6563 | 23.6342 | 12.6606 | 1.9868 | 0.66957 | 9.1237 | 7.4086 | 7.3674 | 7.3413 | 4.6266 | 3.0773 | 0.17802 | 6.4223 | 9.6229 | 51.5312 | 59.5627 | 59.6
40 | 59.1891 | 59.4583 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 53.497 | 18.6636 | 8.9985 | 3.8197 | 2.3748 | 4.1967 | 9.6507 | 20.2193 | 52.7083 | 59.6 | 59.6 | 59.6 | 59.5163 | 59.6
41 | 58.5254 | 56.7778 | 56.4459 | 55.2654 | 53.4897 | 42.0103 | 33.4712 | 12.594 | 0 | 11.1571 | 49.2558 | 40.0357 | 18.144 | 14.0041 | 18.61 | 23.7592 | 32.973 | 32.1783 | 29.4287 | 5.7229 | 5.4972 | 1.9251 | 1.0606 | 0.12013
42 | 0.20475 | 0.040043 | 0.49717 | 0.55386 | 0.71493 | 0.9414 | 1.5221 | 2.0624 | 1.7907 | 4.8943 | 4.3912 | 6.4088 | 8.8797 | 8.1241 | 10.703 | 14.5485 | 15.0884 | 15.5935 | 18.3408 | 12.7655 | 7.6454 | 5.9051 | 7.291 | 4.6555
43 | 0.60035 | 4.726 | 9.694 | 7.0374 | 5.1947 | 3.9356 | 8.0111 | 12.1232 | 14.0427 | 17.4215 | 17.1678 | 6.869 | 1.1035 | 0 | 0 | 0 | 0 | 1.3587 | 0.99541 | 0 | 0 | 0 | 1.6076 | 21.1752
44 | 49.9046 | 52.0563 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 48.831 | 18.911 | 0.99917 | 0 | 0 | 0 | 0 | 0 | 0.24587 | 22.223 | 52.619 | 59.1381 | 59.5547 | 59.6
45 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 58.8708 | 59.3985 | 59.5346 | 57.6482 | 25.6769 | 7.9177 | 9.6505 | 26.0337 | 57.255 | 56.8631 | 25.8704 | 19.9576 | 20.0185 | 12.5477 | 10.707 | 5.6491 | 5.5165 | 2.9859
46 | 59.6 | 59.6 | 59.2245 | 54.51 | 49.4804 | 40.9542 | 42.1622 | 56.7724 | 59.6 | 58.9771 | 55.0844 | 52.7717 | 50.8956 | 48.2762 | 28.9541 | 10.1304 | 45.0267 | 39.1421 | 43.8135 | 19.6214 | 28.0858 | 14.915 | 12.6934 | 13.4951
47 | 16.1976 | 18.9673 | 24.2203 | 25.4846 | 25.3068 | 24.2784 | 18.9559 | 14.1472 | 6.84 | 1.8543 | 1.8511 | 4.0431 | 2.249 | 1.5357 | 8.1468 | 21.9569 | 19.3491 | 22.5685 | 27.979 | 15.8934 | 9.68 | 7.2867 | 8.4404 | 6.8174
48 | 2.3605 | 0.16023 | 0.35639 | 3.0203 | 10.6032 | 18.1875 | 24.4824 | 18.0809 | 10.8541 | 4.9228 | 0.3059 | 0.71934 | 8.6044 | 7.2991 | 0.5652 | 0 | 1.2281 | 8.1233 | 15.3375 | 17.9021 | 10.156 | 0.12532 | 4.0814 | 12.2209
49 | 20.8834 | 32.1533 | 34.3667 | 26.6135 | 23.7133 | 14.4667 | 9.9192 | 4.4252 | 0.94612 | 0.080086 | 0 | 0.57308 | 5.2797 | 7.3806 | 12.8043 | 16.1374 | 12.7791 | 13.2628 | 16.7003 | 26.699 | 47.038 | 26.8496 | 14.5003 | 12.5146
50 | 29.5323 | 37.9516 | 23.6585 | 5.0761 | 1.6237 | 11.1452 | 19.7808 | 26.2839 | 23.9321 | 24.7528 | 14.1136 | 3.3331 | 1.6143 | 19.5751 | 20.3692 | 36.2541 | 55.9051 | 42.4735 | 24.2869 | 5.7411 | 5.8854 | 27.4444 | 39.9206 | 49.3255
51 | 34.1934 | 24.6558 | 59.5838 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 56.8672 | 31.6269 | 7.5242 | 0.71081 | 19.3173 | 59.3211 | 59.6 | 59.5535 | 59.6 | 59.6 | 59.6 | 59.1599 | 56.145 | 59.4496 | 59.6
52 | 59.5275 | 59.6 | 59.6 | 59.6 | 59.6 | 59.5997 | 57.3414 | 54.4287 | 54.9336 | 52.4485 | 50.4511 | 44.9987 | 40.302 | 37.3695 | 38.0699 | 36.5603 | 30.3335 | 25.7201 | 49.4304 | 53.8457 | 33.5109 | 52.2084 | 51.5487 | 50.9648
53 | 59.6 | 59.6 | 59.6 | 59.6 | 59.5123 | 56.2666 | 59.6 | 59.6 | 59.6 | 59.6 | 59.4991 | 26.8983 | 31.9482 | 59.3905 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 56.9738 | 22.9293 | 6.607 | 54.1452 | 51.3651
54 | 18.7445 | 9.5108 | 2.0002 | 3.0752 | 11.062 | 20.4859 | 6.2285 | 3.6648 | 4.3423 | 2.8586 | 3.8367 | 0.93693 | 0 | 1.6636 | 0.93305 | 0.3799 | 0 | 7.1628 | 53.8724 | 59.6 | 59.6 | 59.5621 | 52.969 | 56.5454
55 | 58.8865 | 59.3858 | 59.6 | 59.6 | 59.6 | 59.5744 | 59.3133 | 59.0374 | 57.5544 | 46.1412 | 45.4229 | 53.1811 | 40.556 | 44.9508 | 42.8752 | 46.6805 | 41.3987 | 46.7996 | 58.9672 | 54.7756 | 59.6 | 57.6434 | 10.4499 | 2.0593
56 | 3.7298 | 7.6384 | 10.7236 | 17.3523 | 28.9245 | 46.0564 | 58.7519 | 59.4787 | 59.5723 | 57.9087 | 58.2544 | 56.1997 | 6.8138 | 1.7222 | 18.149 | 16.2495 | 23.8843 | 7.2236 | 13.4278 | 13.08 | 17.1129 | 33.6185 | 50.2832 | 29.7668
57 | 45.8009 | 49.7877 | 58.4148 | 59.0526 | 59.6 | 59.4292 | 58.5604 | 57.5284 | 51.3859 | 53.7794 | 47.1303 | 57.06 | 59.6 | 59.6 | 56.2063 | 49.3551 | 52.6317 | 32.6062 | 18.1349 | 6.8683 | 9.2877 | 12.1171 | 25.0393 | 21.0523
58 | 21.755 | 44.7378 | 55.9283 | 57.9189 | 57.9898 | 53.1764 | 33.5712 | 16.9395 | 7.0145 | 4.4839 | 13.8911 | 54.3731 | 49.4109 | 44.1274 | 41.361 | 36.4014 | 31.2727 | 17.753 | 17.677 | 20.2965 | 13.964 | 6.0061 | 1.2326 | 0
59 | 0 | 0 | 0 | 0.081638 | 1.2828 | 2.8392 | 3.6405 | 6.6141 | 9.1795 | 6.5875 | 9.2713 | 13.5046 | 14.0056 | 12.639 | 14.9875 | 13.1476 | 12.1893 | 12.6155 | 17.8573 | 15.8143 | 9.7726 | 5.8364 | 2.5115 | 4.9616
60 | 19.2633 | 5.942 | 1.4479 | 0.37578 | 4.0833 | 5.3325 | 4.5439 | 0.56806 | 0.38056 | 0.51018 | 14.8022 | 11.3786 | 4.4867 | 5.8862 | 7.2228 | 21.3772 | 51.9642 | 58.7599 | 59.4811 | 56.2873 | 17.0132 | 7.2938 | 25.8729 | 42.4863
61 | 41.5473 | 45.1019 | 59.2377 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 50.6272 | 32.3354 | 27.1694 | 18.1933 | 17.2837 | 24.4909 | 41.3683 | 58.1453 | 52.8886 | 45.6909 | 34.7412 | 58.9372 | 58.9704 | 59.2041 | 50.5296
62 | 13.6769 | 26.8951 | 59.6 | 58.3572 | 26.434 | 29.5475 | 46.9605 | 59.6 | 59.6 | 47.2144 | 39.5262 | 44.9142 | 57.1135 | 59.6 | 59.6 | 59.6 | 59.6 | 59.4847 | 59.6 | 58.3462 | 41.6115 | 21.4013 | 9.6828 | 7.5982
63 | 4.5085 | 0 | 0 | 0.19777 | 0.31497 | 2.4576 | 9.8956 | 12.6346 | 4.5477 | 0.48279 | 1.0529 | 10.181 | 24.6839 | 59.6 | 59.6 | 59.6 | 27.9367 | 36.0947 | 31.0564 | 36.4834 | 5.2166 | 16.4886 | 41.5654 | 9.2011
64 | 1.3585 | 0 | 0.18709 | 18.0879 | 44.5657 | 54.788 | 56.3735 | 56.0664 | 48.6533 | 35.6235 | 42.8446 | 40.7252 | 20.2037 | 9.5271 | 6.5582 | 13.7295 | 32.5113 | 39.1435 | 45.6805 | 50.4886 | 47.3077 | 39.9532 | 40.2645 | 49.2115
65 | 55.6251 | 52.0046 | 47.0988 | 55.5617 | 59.5795 | 58.2709 | 53.0273 | 46.9235 | 45.0567 | 45.2257 | 22.3198 | 12.4592 | 3.0167 | 0.37113 | 0.64761 | 0.18082 | 0 | 0 | 6.1089 | 52.4745 | 47.8123 | 44.6393 | 46.2464 | 48.436
66 | 51.4037 | 52.7446 | 57.0719 | 59.1231 | 59.6 | 59.6 | 59.6 | 59.0003 | 59.3758 | 53.3919 | 18.9128 | 5.209 | 0 | 0 | 4.699 | 12.0596 | 23.0075 | 17.3765 | 21.2087 | 54.2195 | 49.7314 | 32.2479 | 8.5235 | 8.4877
67 | 58.1153 | 56.9371 | 59.0039 | 58.1275 | 59.5842 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 58.9613 | 58.7067 | 59.6 | 59.6 | 59.6 | 56.6275 | 24.4668 | 10.0532 | 24.3635
68 | 41.3961 | 47.0707 | 50.8387 | 44.6162 | 44.166 | 57.3059 | 59.2824 | 59.6 | 59.6 | 55.4906 | 44.592 | 43.4756 | 58.105 | 56.0862 | 51.1659 | 48.9173 | 40.6015 | 59.6 | 59.6 | 13.1246 | 6.1572 | 59.6 | 59.6 | 59.6
69 | 59.6 | 59.6 | 59.5634 | 56.4452 | 37.3506 | 22.7829 | 15.389 | 11.4174 | 2.7806 | 0.040043 | 13.2258 | 7.2684 | 10.1824 | 8.6936 | 3.272 | 15.412 | 4.9146 | 49.3597 | 59.6 | 56.4242 | 36.0996 | 19.949 | 8.2238 | 1.6816
70 | 2.6789 | 7.9632 | 12.3865 | 20.5135 | 34.4702 | 45.6538 | 46.3958 | 44.966 | 36.5827 | 31.202 | 15.9847 | 0.45402 | 0.16023 | 14.8397 | 6.0676 | 35.4925 | 1.1711 | 11.7619 | 54.8858 | 17.896 | 19.9326 | 23.1041 | 25.9792 | 24.1378
71 | 19.3103 | 13.9469 | 26.7587 | 23.7863 | 19.1356 | 14.7252 | 8.3781 | 5.7292 | 8.8767 | 4.3757 | 12.2019 | 12.1245 | 10.9042 | 12.8551 | 16.1064 | 7.7558 | 20.7651 | 27.909 | 23.1199 | 15.0933 | 9.0785 | 0.30006 | 0.50152 | 0.084502
72 | 0.32017 | 0.20893 | 0.65656 | 2.7661 | 3.4231 | 2.6715 | 1.865 | 0.97637 | 0.54431 | 1.0594 | 4.0968 | 5.417 | 7.1283 | 7.241 | 51.2785 | 44.2075 | 19.7961 | 15.9498 | 16.6507 | 8.4172 | 14.7414 | 28.9016 | 0.80623 | 0.39303
73 | 5.3664 | 11.6818 | 25.4988 | 41.98 | 41.2841 | 40.4581 | 18.1265 | 11.1236 | 14.7093 | 10.0332 | 2.1944 | 2.0919 | 0.74996 | 30.3648 | 5.8397 | 17.373 | 13.4736 | 34.8059 | 7.1597 | 10.5635 | 0 | 0 | 5.442 | 0.53214
74 | 6.3185 | 20.8225 | 26.6894 | 28.1458 | 54.4549 | 58.572 | 58.1787 | 59.6 | 59.6 | 58.9893 | 35.3187 | 15.0218 | 1.2646 | 0 | 0.040043 | 0.5942 | 1.1117 | 7.0857 | 17.8616 | 43.8688 | 56.4236 | 33.1468 | 12.9373 | 3.1873
75 | 25.8157 | 46.2711 | 59.588 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 59.5573 | 52.5284 | 26.4665 | 3.8631 | 1.611 | 2.6837 | 2.2277 | 30.6367 | 13.6794 | 32.3707 | 40.9222 | 13.9718
76 | 39.2333 | 23.3955 | 15.7772 | 16.0143 | 15.9189 | 11.584 | 9.2121 | 3.2403 | 2.491 | 6.9245 | 3.3588 | 2.0831 | 2.7502 | 1.8576 | 2.1627 | 5.7222 | 11.9947 | 16.1533 | 15.8934 | 12.0072 | 11.0533 | 6.0795 | 2.7818 | 0.16023
77 | 3.3898 | 6.1237 | 5.773 | 5.206 | 9.053 | 12.764 | 25.982 | 30.6947 | 49.1399 | 55.4086 | 21.6463 | 14.5323 | 1.9432 | 5.409 | 5.6003 | 9.4443 | 7.7806 | 0.16584 | 5.1894 | 0 | 0.48875 | 3.2431 | 0.38539 | 3.684
78 | 5.9304 | 4.0544 | 8.0647 | 8.015 | 9.3151 | 7.5282 | 2.9727 | 5.449 | 7.3819 | 24.4255 | 29.0017 | 14.5584 | 2.2703 | 19.8757 | 59.6 | 29.2868 | 13.4293 | 10.382 | 8.7613 | 11.6298 | 6.3235 | 2.9252 | 0.19664 | 0
79 | 0.43773 | 2.7527 | 6.2422 | 7.5509 | 10.9226 | 10.4322 | 7.4715 | 4.9128 | 4.6309 | 2.7097 | 2.1843 | 1.9566 | 0.84753 | 0.26771 | 0.2581 | 0.80564 | 1.8004 | 2.5735 | 4.1108 | 3.4869 | 7.7847 | 5.8636 | 5.2539 | 11.0585
80 | 28.8418 | 40.9367 | 28.0226 | 40.9897 | 28.1484 | 18.4201 | 14.6385 | 17.0509 | 17.4482 | 5.2595 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.17366 | 3.563 | 2.6186 | 1.0264 | 0.8384 | 0 | 8.5306
81 | 1.7121 | 1.6698 | 4.1449 | 4.309 | 5.7841 | 24.6114 | 35.2911 | 22.5637 | 31.2366 | 20.626 | 13.4747 | 10.4764 | 4.814 | 2.8276 | 11.7226 | 14.8306 | 15.6831 | 14.4057 | 8.7324 | 4.5625 | 1.0997 | 1.6911 | 7.369 | 39.1109
82 | 41.7895 | 19.3238 | 1.0865 | 0.35961 | 55.3832 | 59.6 | 59.0297 | 54.0205 | 42.8106 | 33.0099 | 27.2565 | 26.6618 | 24.3449 | 39.6379 | 54.3954 | 59.1075 | 59.6 | 59.3916 | 59.4671 | 59.5402 | 59.3217 | 59.1603 | 59.6 | 59.6
83 | 59.6 | 33.0972 | 28.6459 | 41.374 | 54.8258 | 51.1739 | 42.3696 | 34.1988 | 8.641 | 0 | 1.9838 | 12.6717 | 20.8677 | 11.9972 | 26.5875 | 41.1441 | 59.3581 | 59.6 | 53.9457 | 43.943 | 16.915 | 2.0363 | 2.8293 | 5.3545
84 | 5.9822 | 0.040043 | 1.5338 | 1.9185 | 3.8219 | 3.4023 | 4.7301 | 5.6432 | 4.0481 | 5.5739 | 6.4887 | 8.5141 | 11.0057 | 9.8862 | 14.0435 | 15.7778 | 32.2633 | 52.8173 | 46.957 | 36.3414 | 3.6341 | 0.080086 | 10.1828 | 7.2416
85 | 4.4419 | 1.5414 | 12.8811 | 50.0955 | 57.4813 | 58.5705 | 58.2704 | 59.385 | 59.34 | 56.0565 | 40.5864 | 12.2803 | 7.7384 | 5.6914 | 8.5045 | 19.908 | 11.0382 | 3.5141 | 0.040043 | 4.3244 | 3.214 | 42.0369 | 46.0209 | 45.5979
86 | 44.766 | 38.7684 | 22.9022 | 15.3236 | 14.0039 | 15.3335 | 6.8258 | 6.0141 | 3.6576 | 0.17229 | 0.77687 | 56.7652 | 59.6 | 59.6 | 57.9744 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 59.5964 | 37.1812 | 13.0047
87 | 6.3914 | 0.68163 | 1.1739 | 2.0332 | 2.5209 | 5.3444 | 4.926 | 9.2519 | 41.3634 | 58.5972 | 58.2912 | 59.6 | 59.6 | 59.6 | 59.6 | 58.2125 | 59.484 | 57.7574 | 59.3143 | 59.6 | 59.6 | 59.6 | 59.6 | 57.7805
88 | 54.7077 | 59.2847 | 59.6 | 59.6 | 59.6 | 54.2973 | 9.2433 | 1.7717 | 2.8179 | 5.7913 | 3.7728 | 4.7068 | 5.3559 | 10.5006 | 17.1977 | 28.6792 | 31.2316 | 51.8809 | 28.2243 | 10.1578 | 23.2942 | 21.0342 | 33.4561 | 28.8879
89 | 25.479 | 25.7853 | 32.3693 | 39.0625 | 24.3691 | 6.9497 | 1.2553 | 1.195 | 3.7288 | 6.7486 | 3.0556 | 3.5211 | 1.9675 | 3.3556 | 7.2785 | 14.542 | 14.0446 | 15.3145 | 13.593 | 10.4874 | 6.8451 | 4.7333 | 4.5091 | 2.8601
90 | 3.4765 | 5.6972 | 10.5338 | 12.4523 | 13.1044 | 10.1683 | 11.6523 | 11.4091 | 5.3356 | 0 | 0 | 0 | 0.63299 | 2.3887 | 6.4431 | 8.4147 | 10.0387 | 7.1188 | 6.6891 | 3.3996 | 0 | 1.7277 | 59.6 | 59.6
91 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 57.8117 | 46.8695 | 27.5774 | 51.8451 | 59.5756 | 57.457 | 47.6593 | 48.349 | 49.3432 | 27.4867 | 38.473 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6
92 | 59.6 | 25.152 | 23.3156 | 5.2542 | 3.5845 | 33.5535 | 18.7562 | 12.7171 | 10.3874 | 11.1301 | 10.3761 | 9.6293 | 10.2597 | 12.7878 | 15.2137 | 22.6965 | 26.1106 | 20.9544 | 17.7317 | 26.8536 | 24.276 | 24.9545 | 19.3547 | 15.8774
93 | 16.5188 | 17.0399 | 20.2431 | 20.1949 | 23.4649 | 22.8867 | 16.2472 | 11.5578 | 7.1509 | 0.080086 | 0 | 0 | 0 | 0 | 4.3873 | 5.8395 | 4.3107 | 8.4388 | 17.0595 | 26.9233 | 26.7044 | 35.5313 | 20.4573 | 13.2952
94 | 23.2507 | 5.5584 | 22.3622 | 0.70645 | 2.0864 | 12.2726 | 13.5373 | 5.7882 | 6.5582 | 3.4694 | 0.9078 | 3.0217 | 5.2857 | 10.5009 | 12.421 | 14.114 | 15.9664 | 15.7419 | 14.7986 | 13.5882 | 7.1476 | 1.4897 | 0.080086 | 1.0425
95 | 5.4829 | 18.6707 | 27.9616 | 47.1791 | 55.6535 | 58.2301 | 57.1048 | 56.4063 | 54.0728 | 31.2119 | 8.071 | 0.51119 | 10.987 | 7.8055 | 38.283 | 17.7425 | 35.071 | 8.9189 | 23.0785 | 1.4018 | 15.9908 | 1.9043 | 22.5473 | 6.1039
96 | 0.42353 | 9.5534 | 36.9695 | 59.6 | 59.0656 | 59.0129 | 54.9221 | 54.2486 | 47.8375 | 56.2215 | 47.9734 | 39.2962 | 24.7345 | 17.292 | 30.3131 | 9.2109 | 3.8333 | 14.8334 | 54.3611 | 59.3584 | 50.6342 | 40.4484 | 48.0654 | 32.3369
97 | 18.6377 | 18.8934 | 34.5121 | 27.8164 | 33.8375 | 24.1563 | 35.1741 | 55.9725 | 51.6028 | 45.5922 | 36.3215 | 18.3132 | 10.1813 | 10.5328 | 56.6911 | 59.6 | 31.8979 | 34.2529 | 18.0281 | 48.7576 | 0 | 0.43296 | 22.0934 | 34.6273
98 | 32.0407 | 37.212 | 50.2723 | 55.8128 | 44.5556 | 46.4641 | 43.2727 | 28.191 | 42.1455 | 55.4408 | 42.8927 | 30.8217 | 29.1024 | 20.1173 | 5.9784 | 4.0093 | 6.0953 | 0 | 4.0733 | 20.6764 | 55.6987 | 59.3778 | 58.3399 | 57.2295
99 | 54.0107 | 47.552 | 42.6488 | 17.3785 | 1.9931 | 0.42752 | 2.8419 | 3.6895 | 0.94564 | 1.5224 | 1.5265 | 1.3913 | 2.0904 | 3.8441 | 0.26276 | 0 | 4.4157 | 6.834 | 4.7643 | 14.3697 | 27.8044 | 18.2012 | 27.9367 | 21.8537
100 | 19.2091 | 27.2164 | 36.3825 | 42.7242 | 12.6411 | 1.5344 | 0 | 0.20028 | 1.9845 | 30.635 | 45.0298 | 41.0627 | 23.7983 | 12.357 | 16.9968 | 17.4929 | 2.7133 | 5.5655 | 10.8736 | 42.2863 | 54.6952 | 54.1638 | 59.6 | 59.6
101 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 59.489 | 59.6 | 59.6 | 59.6 | 59.0236 | 46.3387 | 14.5463
102 | 36.5321 | 20.1911 | 0 | 0 | 6.0077 | 24.031 | 26.4753 | 24.031 | 24.031 | 20.4263 | 24.031 | 24.031 | 59.6 | 59.6 | 59.5977 | 59.3996 | 58.9112 | 44.8313 | 10.6755 | 50.1975 | 58.6556 | 34.6823 | 24.6388 | 39.8744
103 | 38.1276 | 44.0518 | 31.437 | 34.5738 | 24.7776 | 28.3153 | 15.8747 | 1.4993 | 1.2318 | 1.1375 | 5.3222 | 27.3517 | 46.5445 | 43.3927 | 36.1624 | 38.0362 | 38.8283 | 46.8842 | 59.3902 | 59.6 | 58.2916 | 59.6 | 59.6 | 59.6
104 | 44.6107 | 24.2688 | 23.5414 | 36.0529 | 36.9206 | 55.4575 | 58.0572 | 58.9052 | 57.6577 | 47.5855 | 55.8593 | 59.6 | 56.3647 | 41.2835 | 44.6805 | 49.7287 | 53.8832 | 53.4085 | 41.0741 | 40.5872 | 32.3096 | 59.0411 | 59.6 | 59.6
105 | 0 | 1.2108 | 5.1304 | 8.7329 | 1.8389 | 3.3372 | 7.1173 | 0.95352 | 4.4093 | 10.4306 | 12.638 | 16.3105 | 23.3101 | 56.1065 | 54.0243 | 31.1755 | 52.5505 | 35.2214 | 20.7545 | 29.9536 | 33.2792 | 45.6112 | 28.997 | 15.5112
106 | 15.7878 | 1.7367 | 20.2671 | 32.886 | 18.7793 | 20.4462 | 3.7426 | 2.8756 | 10.2382 | 23.4355 | 10.1685 | 44.2494 | 23.5207 | 27.9015 | 46.3244 | 42.7788 | 52.2621 | 37.5481 | 38.2111 | 42.9306 | 28.5927 | 16.1546 | 8.0117 | 0.72513
107 | 1.9788 | 1.5711 | 1.7658 | 5.8126 | 1.4518 | 2.0413 | 10.3401 | 14.3126 | 12.4023 | 12.4467 | 8.0043 | 1.9858 | 0.83727 | 1.8597 | 1.9729 | 53.8432 | 8.583 | 13.8714 | 12.8771 | 59.4749 | 59.5064 | 22.5645 | 1.939 | 6.7426
108 | 1.6952 | 10.2225 | 18.5126 | 16.836 | 10.7895 | 10.0035 | 10.8437 | 14.7731 | 35.0658 | 48.2832 | 35.2035 | 40.0048 | 32.273 | 42.9994 | 42.8082 | 16.6892 | 10.4147 | 5.3356 | 0.78952 | 0 | 0 | 0 | 0.87916 | 0
109 | 0 | 4.0349 | 26.2908 | 59.6 | 57.2688 | 58.5735 | 59.3565 | 59.4129 | 57.1759 | 39.7462 | 8.1988 | 2.6628 | 0.44865 | 1.2777 | 7.6467 | 7.3576 | 15.3205 | 11.2732 | 38.7067 | 52.0306 | 3.8332 | 2.223 | 5.875 | 12.7171
110 | 19.7835 | 13.4306 | 17.6865 | 17.2168 | 15.3081 | 25.1453 | 18.6646 | 10.9131 | 11.3632 | 5.5634 | 3.5664 | 5.0232 | 2.9457 | 2.8173 | 7.1759 | 1.3761 | 4.4132 | 2.274 | 4.5453 | 13.4216 | 10.99 | 6.9647 | 0.63454 | 0
111 | 0 | 0.040043 | 1.8876 | 6.9557 | 11.3414 | 7.591 | 11.4447 | 16.9894 | 5.9059 | 8.5331 | 5.6943 | 6.1406 | 4.5085 | 4.9352 | 8.7804 | 4.1062 | 4.2872 | 8.7301 | 10.3403 | 24.6198 | 22.0042 | 17.4767 | 9.2615 | 1.3909
112 | 54.2272 | 55.1301 | 58.2126 | 31.6586 | 53.203 | 46.4118 | 23.695 | 16.3683 | 31.5655 | 11.2897 | 6.5378 | 0.31193 | 0 | 0.28036 | 8.0241 | 9.9576 | 15.1491 | 5.6346 | 42.9638 | 54.8068 | 55.5608 | 32.0961 | 44.7408 | 55.948
113 | 41.0118 | 27.0723 | 23.834 | 13.9132 | 1.9153 | 0.054604 | 2.9985 | 16.2484 | 21.6059 | 9.7083 | 0 | 4.6003 | 8.9096 | 47.57 | 46.342 | 59.6 | 59.6 | 59.6 | 59.6 | 22.0202 | 5.1835 | 15.1891 | 3.0004 | 55.8894
114 | 27.877 | 54.0323 | 35.9513 | 37.2633 | 2.9931 | 15.1794 | 50.7853 | 37.584 | 59.5843 | 59.6 | 40.0349 | 18.5409 | 57.2592 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 59.2063 | 59.6 | 57.9212
115 | 49.91 | 47.594 | 30.8273 | 17.4365 | 20.3167 | 21.1713 | 25.6725 | 19.3388 | 58.6488 | 59.6 | 59.6 | 59.6 | 57.8754 | 54.2866 | 50.4046 | 42.5039 | 32.0479 | 14.2329 | 10.1976 | 15.4053 | 12.2301 | 8.9294 | 3.2263 | 0.43122
116 | 0.080086 | 4.9512 | 9.7791 | 9.7196 | 4.682 | 12.3644 | 25.573 | 44.0254 | 22.1168 | 5.0981 | 0 | 0 | 0 | 0.14931 | 2.2765 | 1.6368 | 4.0481 | 2.0124 | 10.3086 | 14.6812 | 36.9515 | 59.6 | 9.1124 | 43.9057
117 | 23.7398 | 12.0844 | 18.3287 | 29.6538 | 24.5874 | 13.5966 | 6.9424 | 0.66116 | 0.1227 | 0 | 0 | 0.080086 | 1.0713 | 0.76697 | 1.4583 | 2.7974 | 7.0737 | 12.7153 | 19.5033 | 40.8863 | 48.7743 | 56.5329 | 27.1 | 43.9751
118 | 56.5742 | 59.1548 | 59.6 | 50.3971 | 23.9022 | 19.0592 | 15.2018 | 6.3136 | 1.9776 | 1.0801 | 0 | 0.080086 | 2.5297 | 6.1665 | 10.5227 | 11.4559 | 13.513 | 6.1538 | 13.5159 | 21.2144 | 31.7103 | 32.2693 | 4.7975 | 5.2849
119 | 38.1205 | 40.5598 | 35.4466 | 56.7904 | 59.3312 | 59.6 | 59.6 | 59.6 | 56.2735 | 30.5478 | 3.6222 | 0 | 0 | 0.64081 | 4.6981 | 9.7076 | 21.0173 | 30.0479 | 54.0298 | 58.14 | 59.6 | 59.6 | 59.6 | 49.4969
120 | 20.9638 | 42.7634 | 53.758 | 25.9332 | 6.0125 | 8.4647 | 8.6436 | 8.7757 | 1.1984 | 0 | 0 | 1.1998 | 3.2288 | 8.1277 | 7.5775 | 5.3923 | 2.6997 | 0.98431 | 1.088 | 0.9315 | 1.5086 | 17.4694 | 38.268 | 32.6699
121 | 8.7128 | 3.3744 | 0.12896 | 0.16208 | 0.48905 | 24.0254 | 45.1371 | 31.3869 | 59.6 | 59.6 | 57.0735 | 42.7312 | 59.6 | 59.6 | 59.6 | 57.7738 | 50.3591 | 59.6 | 59.6 | 59.6 | 59.6 | 59.5628 | 50.3084 | 38.974
122 | 33.0568 | 25.3038 | 31.8909 | 45.458 | 48.1521 | 34.4909 | 49.6587 | 57.2703 | 59.6 | 59.6 | 59.6 | 48.2917 | 13.7824 | 2.5444 | 0.84705 | 0 | 33.5825 | 9.6522 | 6.0674 | 2.0581 | 1.1112 | 6.3873 | 5.0129 | 4.0858
123 | 3.1356 | 5.698 | 8.7677 | 9.1426 | 5.4798 | 1.1098 | 0.40133 | 1.6567 | 6.4603 | 20.7302 | 37.7644 | 17.5393 | 6.7147 | 18.5422 | 21.8683 | 24.1096 | 20.8841 | 56.2765 | 38.2985 | 25.2502 | 24.4771 | 4.0971 | 4.7154 | 0
124 | 5.7891 | 6.8569 | 16.8995 | 22.7021 | 18.2357 | 14.8032 | 12.5362 | 19.663 | 7.4184 | 0.45313 | 0 | 0 | 5.3787 | 2.1986 | 2.6393 | 30.1651 | 6.8564 | 9.2565 | 59.2843 | 59.6 | 59.6 | 59.1545 | 53.2293 | 52.4707
125 | 42.5236 | 38.7535 | 30.5294 | 23.7736 | 26.3875 | 27.8571 | 24.7493 | 3.3784 | 3.7093 | 0 | 0 | 0.99481 | 5.9368 | 14.6706 | 22.737 | 38.1341 | 59.6 | 20.8047 | 5.0547 | 23.9509 | 57.5893 | 58.5613 | 47.9234 | 15.039
126 | 10.8148 | 11.6597 | 5.159 | 7.0569 | 8.2213 | 21.0923 | 42.5426 | 34.9145 | 42.3565 | 52.9764 | 38.1718 | 20.495 | 5.4248 | 0.73349 | 27.2308 | 13.575 | 18.7515 | 59.5957 | 26.1065 | 53.2377 | 5.4823 | 6.2972 | 40.3038 | 55.6449
127 | 53.7286 | 57.1115 | 59.5862 | 58.8221 | 56.6461 | 54.498 | 52.3911 | 39.3377 | 2.7447 | 13.0163 | 16.0863 | 16.8564 | 10.5676 | 4.9707 | 1.251 | 10.548 | 14.0418 | 24.4835 | 41.1299 | 22.8869 | 5.1522 | 3.7031 | 2.8298 | 12.8996
128 | 48.7097 | 58.3565 | 13.6606 | 33.4015 | 38.4347 | 2.5087 | 2.2276 | 9.9799 | 1.8589 | 4.3738 | 17.2671 | 59.6 | 18.408 | 0.44059 | 0.95185 | 49.6882 | 7.1817 | 6.9387 | 57.4169 | 59.6 | 25.1594 | 25.832 | 0.080086 | 0.53518
129 | 2.471 | 13.9661 | 39.6378 | 53.5535 | 53.8156 | 55.1592 | 58.2926 | 45.421 | 33.6479 | 33.5647 | 26.1891 | 25.2876 | 18.098 | 13.1085 | 44.6787 | 3.9001 | 59.6 | 59.6 | 59.3793 | 59.6 | 58.2557 | 40.2512 | 40.7973 | 39.1169
130 | 14.0602 | 15.3153 | 46.2897 | 56.7722 | 42.5616 | 44.4901 | 32.2261 | 11.0803 | 7.9583 | 5.1475 | 7.2379 | 3.2245 | 2.0752 | 12.0584 | 12.0597 | 54.0117 | 35.8375 | 59.4062 | 59.1167 | 0 | 0.70317 | 1.7452 | 3.5884 | 5.9853
131 | 9.1528 | 33.2468 | 52.9143 | 55.5274 | 48.7008 | 49.2075 | 48.4694 | 28.6282 | 21.9812 | 9.0687 | 1.0358 | 0.24032 | 0 | 0.3204 | 2.0392 | 28.3692 | 37.583 | 11.2188 | 35.6663 | 59.6 | 59.6 | 55.8574 | 53.6808 | 58.8143
132 | 52.1529 | 43.5461 | 53.9135 | 55.6675 | 57.7765 | 58.3231 | 57.0979 | 32.0876 | 10.0426 | 0.40049 | 0.080086 | 3.0824 | 12.0606 | 25.1308 | 58.8555 | 53.1247 | 55.4189 | 38.292 | 36.2985 | 35.9081 | 7.268 | 7.3453 | 1.7497 | 2.5782
133 | 1.1507 | 3.123 | 6.9616 | 3.9306 | 7.2783 | 6.3123 | 0.72018 | 0.057827 | 3.0082 | 0 | 2.1588 | 2.4919 | 3.9148 | 26.2198 | 29.928 | 28.8215 | 58.7731 | 43.4949 | 36.2226 | 55.513 | 58.1197 | 59.6 | 59.6 | 53.9971
134 | 26.2347 | 10.3947 | 10.6453 | 11.3532 | 7.0419 | 2.5989 | 0 | 0 | 0 | 3.0082 | 8.132 | 9.2433 | 12.4198 | 5.9865 | 13.5272 | 36.9479 | 48.1573 | 57.2313 | 59.6 | 27.4172 | 45.692 | 14.5002 | 17.5613 | 3.1598
135 | 4.7793 | 2.5034 | 3.4622 | 5.9972 | 0.48583 | 0 | 0.040043 | 2.689 | 20.8833 | 18.767 | 12.4064 | 6.3025 | 1.3151 | 53.631 | 58.7938 | 56.9446 | 56.5536 | 57.7819 | 59.6 | 59.6 | 30.0516 | 25.6077 | 16.6143 | 8.9728
136 | 4.9886 | 2.2934 | 0.81787 | 0.61712 | 0.58591 | 2.2847 | 2.7323 | 0 | 0 | 0 | 0.41117 | 40.4149 | 53.9258 | 56.9769 | 56.9075 | 59.6 | 51.695 | 58.3713 | 57.3279 | 35.8769 | 11.2574 | 16.8157 | 10.0777 | 6.5384
137 | 3.8391 | 6.6806 | 2.7601 | 7.6145 | 4.0706 | 3.9215 | 10.3021 | 3.3226 | 9.3981 | 14.5927 | 23.9018 | 23.1644 | 15.1872 | 13.3844 | 16.5545 | 20.884 | 12.8849 | 28.4296 | 18.2267 | 11.9826 | 11.067 | 9.7538 | 12.958 | 12.6031
138 | 14.8579 | 13.2543 | 14.1071 | 10.7991 | 5.6402 | 3.3784 | 5.1467 | 2.9353 | 4.3985 | 6.6174 | 15.4796 | 18.5569 | 11.934 | 17.4417 | 22.0455 | 19.1337 | 28.2856 | 31.0319 | 58.5292 | 59.6 | 50.4499 | 48.0565 | 22.4146 | 28.2659
139 | 27.7492 | 20.4379 | 10.7388 | 19.066 | 33.8272 | 40.1933 | 33.0218 | 22.041 | 32.3438 | 16.8991 | 2.4519 | 0.040043 | 2.2462 | 1.6331 | 1.1872 | 43.183 | 0.77126 | 0.080086 | 10.0243 | 17.075 | 23.3696 | 32.6775 | 17.1102 | 5.4022
140 | 4.2304 | 32.3966 | 54.7904 | 59.0667 | 59.6 | 59.6 | 59.5717 | 55.508 | 48.9167 | 46.2731 | 59.6 | 58.1496 | 10.9202 | 2.9481 | 0.12013 | 1.5871 | 15.5606 | 28.8838 | 51.0836 | 51.6666 | 47.5254 | 24.4044 | 51.884 | 35.438
141 | 43.0668 | 58.9417 | 56.5406 | 30.4658 | 16.1184 | 15.4891 | 18.9837 | 23.7836 | 2.7386 | 0.12013 | 4.5202 | 42.9677 | 48.688 | 59.6 | 57.3603 | 58.5406 | 59.5601 | 59.6 | 59.6 | 59.6 | 59.6 | 59.3455 | 55.5243 | 51.533
142 | 37.3576 | 35.3327 | 22.8712 | 26.3399 | 33.3916 | 37.127 | 25.5634 | 16.228 | 1.7673 | 3.2208 | 1.8337 | 0.73617 | 2.8665 | 6.9442 | 33.4349 | 58.3045 | 32.5375 | 9.5085 | 1.5647 | 59.6 | 16.0473 | 17.0058 | 5.5222 | 1.3991
143 | 0.16023 | 0.21872 | 0 | 2.0441 | 0 | 3.466 | 4.3926 | 4.9082 | 9.0183 | 13.6865 | 20.2445 | 19.6832 | 8.8366 | 18.6385 | 28.5796 | 8.5273 | 32.13 | 48.1687 | 9.407 | 5.3351 | 0.41368 | 4.1641 | 2.5601 | 3.706
144 | 4.7144 | 0.080086 | 1.3499 | 5.1847 | 7.2214 | 3.4689 | 7.7258 | 11.7143 | 7.7957 | 10.2219 | 12.3598 | 17.6787 | 17.1154 | 21.6888 | 32.6267 | 34.8686 | 34.4884 | 46.8837 | 36.374 | 22.6013 | 15.4812 | 14.2011 | 13.0536 | 24.7165
145 | 1.158 | 8.2105 | 14.318 | 11.4873 | 11.7773 | 12.6642 | 11.6216 | 15.4379 | 21.5106 | 28.3544 | 56.6003 | 59.6 | 59.5011 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 59.5501 | 58.4197 | 59.0432 | 42.7743
146 | 22.713 | 25.1436 | 17.7176 | 8.8081 | 11.5874 | 13.4327 | 4.1445 | 2.7897 | 1.3228 | 10.0591 | 14.0349 | 22.8498 | 4.8097 | 1.6425 | 52.9938 | 30.8098 | 54.1594 | 31.3024 | 58.5681 | 53.1247 | 11.11 | 2.5514 | 0 | 1.4325
147 | 21.7604 | 36.3258 | 9.9249 | 11.6007 | 22.1532 | 23.67 | 23.8573 | 8.2778 | 8.676 | 17.4999 | 8.8753 | 11.2188 | 5.9335 | 31.8987 | 57.4624 | 52.0565 | 13.517 | 56.6069 | 10.9694 | 17.8712 | 50.1943 | 7.9156 | 0 | 0
148 | 1.071 | 0.72615 | 0.7385 | 3.3732 | 2.3668 | 5.3743 | 4.7346 | 2.849 | 5.3735 | 4.1814 | 4.6143 | 8.6259 | 8.1827 | 11.3832 | 14.5882 | 40.7924 | 4.5481 | 8.6357 | 54.3817 | 45.7772 | 59.6 | 51.4924 | 16.9431 | 19.2793
149 | 3.2994 | 54.4994 | 15.7189 | 19.1671 | 1.9622 | 0 | 7.9872 | 27.1012 | 32.2317 | 26.0328 | 59.3547 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 56.7074 | 45.4616 | 28.323 | 32.5367 | 26.2428 | 23.7967
150 | 15.8887 | 0.4132 | 0.65107 | 0.083309 | 2.0115 | 5.7676 | 6.718 | 3.9393 | 16.0835 | 36.3682 | 24.2019 | 10.7612 | 6.1993 | 3.3143 | 13.4933 | 10.6331 | 9.8899 | 54.2083 | 59.6 | 10.0155 | 1.8114 | 4.6123 | 5.2243 | 7.3526
151 | 3.5011 | 7.0756 | 33.8919 | 26.0413 | 12.3692 | 13.3169 | 21.8139 | 17.0812 | 17.1851 | 18.1977 | 14.2093 | 6.4446 | 0.69452 | 0 | 0.080086 | 4.8575 | 42.9304 | 19.2292 | 1.6698 | 1.9468 | 4.3543 | 6.8918 | 3.7406 | 11.0998
152 | 41.1568 | 32.0612 | 28.1123 | 21.1119 | 12.2976 | 6.3393 | 1.8192 | 1.9959 | 10.6193 | 12.2123 | 22.2663 | 19.2695 | 12.7356 | 7.4229 | 5.839 | 3.4553 | 2.0093 | 2.5079 | 6.93 | 8.7188 | 28.8716 | 31.8723 | 18.9915 | 15.0167
153 | 25.3506 | 25.7827 | 24.328 | 35.8982 | 52.7227 | 31.1881 | 15.0658 | 9.2674 | 11.894 | 7.8041 | 6.2955 | 4.7247 | 7.2387 | 14.1371 | 27.9609 | 56.1083 | 50.6339 | 41.4445 | 29.7188 | 5.3547 | 13.7551 | 2.8785 | 0.48052 | 0.80838
154 | 0.040043 | 6.1529 | 45.1684 | 14.5299 | 57.3451 | 53.9731 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 55.1441 | 54.0304 | 53.003 | 56.6031 | 42.3067 | 59.0839 | 59.0722 | 57.1225 | 49.3881 | 57.4938 | 58.3555 | 59.6
155 | 59.2698 | 58.9067 | 38.2837 | 12.8732 | 6.6809 | 5.9238 | 5.9986 | 2.8931 | 1.155 | 0 | 0 | 0 | 2.7221 | 16.9536 | 59.6 | 16.7732 | 36.855 | 59.6 | 1.6138 | 20.5307 | 22.3407 | 12.1162 | 5.6032 | 0
156 | 24.5997 | 21.1902 | 11.8935 | 0.39363 | 2.9807 | 9.9463 | 6.386 | 4.9144 | 9.1689 | 9.451 | 12.9589 | 15.2164 | 5.9317 | 8.9246 | 13.8031 | 9.1181 | 20.9953 | 42.8676 | 35.2584 | 22.2894 | 16.9475 | 12.579 | 9.0621 | 6.3793
157 | 2.8571 | 1.6076 | 0.8011 | 0.13493 | 0.2584 | 0 | 0 | 0 | 0 | 0 | 0.85559 | 2.3729 | 7.4557 | 16.5756 | 17.8347 | 16.5927 | 35.2116 | 2.2427 | 59.6 | 29.0115 | 28.2938 | 2.1536 | 28.7342 | 0.7425
158 | 3.5244 | 8.6052 | 11.0592 | 12.4134 | 17.498 | 18.3722 | 22.3398 | 18.0512 | 8.2297 | 0 | 0 | 0.28036 | 8.5951 | 12.3453 | 11.1533 | 11.9174 | 5.0072 | 0.040043 | 53.2497 | 13.9538 | 31.3707 | 35.4148 | 50.7376 | 18.0373
159 | 7.1362 | 5.5368 | 5.8242 | 3.4236 | 3.1945 | 1.7636 | 10.4109 | 6.9965 | 3.7288 | 1.7229 | 0.66581 | 2.6942 | 7.6032 | 8.6821 | 6.6134 | 2.3377 | 3.7855 | 0.080086 | 1.9576 | 3.5995 | 5.5686 | 0 | 0.45354 | 0.040043
160 | 13.2373 | 30.6316 | 30.4081 | 34.0693 | 25.912 | 55.5774 | 58.8224 | 40.6638 | 18.1675 | 9.4273 | 5.5858 | 1.5407 | 0 | 0.30644 | 0 | 0 | 0 | 0 | 52.8352 | 35.0819 | 58.4092 | 44.0346 | 34.1446 | 40.567
161 | 54.359 | 56.8438 | 58.5539 | 59.6 | 59.5897 | 59.5213 | 55.4022 | 35.7621 | 11.4093 | 2.134 | 0 | 0 | 0 | 0 | 0 | 0.38044 | 41.8383 | 56.7044 | 9.0702 | 0.18971 | 42.2727 | 0.17623 | 59.1314 | 22.8248
162 | 44.3839 | 50.154 | 46.6174 | 54.1158 | 45.8782 | 14.1418 | 2.1694 | 19.8205 | 12.1922 | 21.2343 | 2.379 | 1.8278 | 2.3941 | 1.4832 | 59.6 | 59.6 | 34.0747 | 3.0872 | 17.2479 | 23.3989 | 1.3558 | 58.6778 | 11.0211 | 7.0301
163 | 27.386 | 26.166 | 39.1079 | 17.7365 | 4.7963 | 0.92141 | 0.84562 | 0.28036 | 0 | 0 | 0 | 1.5243 | 1.3719 | 1.9513 | 1.7959 | 17.3852 | 6.2243 | 27.684 | 58.7664 | 54.1155 | 59.6 | 33.6439 | 8.136 | 14.6134
164 | 0.12013 | 0.35317 | 0.64129 | 1.7256 | 15.6273 | 26.2879 | 14.0081 | 14.9471 | 8.0987 | 5.5467 | 2.5363 | 0 | 0 | 0 | 6.3139 | 53.17 | 20.3151 | 24.3558 | 33.2664 | 0.81984 | 20.8038 | 59.6 | 42.2489 | 1.2622
165 | 0 | 0.716 | 9.9579 | 5.8879 | 6.4893 | 12.159 | 11.7685 | 3.3561 | 0.97739 | 0 | 0.040043 | 1.9794 | 9.8222 | 23.0573 | 59.6 | 8.9515 | 16.3098 | 15.0739 | 16.4799 | 53.9286 | 4.5807 | 23.0711 | 16.5354 | 7.4789
166 | 2.3753 | 8.6775 | 22.6507 | 16.4579 | 15.8558 | 12.5361 | 6.5636 | 3.9809 | 1.2795 | 0 | 0 | 1.888 | 1.4478 | 1.7826 | 0.69458 | 0.89491 | 2.7302 | 48.3188 | 22.2171 | 30.4655 | 34.1004 | 59.6 | 59.6 | 55.2979
167 | 32.2255 | 52.0655 | 59.6 | 59.6 | 22.2762 | 47.5946 | 50.9443 | 16.7257 | 16.9362 | 14.9496 | 17.692 | 30.1266 | 55.6149 | 58.9597 | 58.5057 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 53.6402 | 59.6 | 59.6
168 | 59.6 | 59.6 | 59.6 | 59.1176 | 37.6971 | 58.6639 | 59.6 | 58.7155 | 54.775 | 44.1859 | 54.7541 | 55.1165 | 47.7705 | 27.0976 | 31.6459 | 21.3774 | 24.7434 | 37.1565 | 29.9633 | 10.8584 | 4.651 | 55.7045 | 59.6 | 59.6
169 | 59.6 | 59.6 | 58.1567 | 45.6821 | 39.3564 | 32.02 | 22.0001 | 20.1576 | 6.0781 | 0 | 0 | 0 | 0 | 5.3873 | 17.1824 | 19.6453 | 16.8451 | 18.6188 | 30.7448 | 35.1239 | 58.8738 | 59.6 | 55.3582 | 52.9012
170 | 19.8215 | 29.7639 | 4.4539 | 33.0466 | 38.2712 | 35.1151 | 36.7629 | 30.7777 | 16.4142 | 19.8582 | 17.4982 | 18.5906 | 7.301 | 6.8789 | 20.3089 | 26.0422 | 29.0195 | 39.2498 | 53.3536 | 58.474 | 59.3819 | 47.3264 | 23.0989 | 15.478
171 | 17.1874 | 10.9086 | 29.4313 | 53.0638 | 58.1464 | 37.3564 | 38.0252 | 28.398 | 7.7024 | 5.5884 | 16.7217 | 34.4038 | 30.343 | 13.1421 | 23.3323 | 13.2649 | 13.2222 | 29.4396 | 58.2882 | 59.6 | 56.2772 | 59.499 | 59.4721 | 58.3651
172 | 53.8698 | 43.3378 | 51.7699 | 58.885 | 52.6791 | 50.6981 | 45.2749 | 24.0991 | 9.3928 | 8.1718 | 2.9344 | 0.41654 | 0 | 7.4025 | 13.488 | 12.971 | 12.4768 | 22.3067 | 27.8316 | 46.798 | 58.0563 | 33.6982 | 49.7707 | 43.4058
173 | 7.3401 | 0.79991 | 0.35573 | 0.20028 | 0 | 0 | 3.4801 | 0 | 2.5358 | 9.9775 | 5.9584 | 23.1064 | 35.442 | 6.9876 | 18.1561 | 8.9636 | 19.5954 | 41.9544 | 3.2612 | 11.7756 | 2.3409 | 1.2024 | 0 | 2.4072
174 | 9.9558 | 0.54193 | 6.6003 | 0.29636 | 0.64254 | 2.3893 | 4.8072 | 0 | 0 | 0 | 0 | 0.24658 | 2.102 | 6.2881 | 9.389 | 11.2546 | 32.6026 | 1.9421 | 18.4237 | 47.9183 | 24.3938 | 0 | 41.4552 | 29.134
175 | 47.956 | 51.1735 | 15.1467 | 12.8815 | 31.161 | 54.4713 | 40.9108 | 12.6578 | 2.5162 | 2.8899 | 7.5423 | 3.7145 | 3.3816 | 5.0778 | 10.4347 | 10.9014 | 17.0901 | 59.6 | 59.6 | 59.0775 | 34.0995 | 5.286 | 12.6726 | 0.16023
176 | 0 | 7.1197 | 8.2948 | 11.8931 | 12.1598 | 8.2333 | 6.2133 | 2.9001 | 0.84025 | 5.0191 | 10.1806 | 22.6789 | 26.8499 | 26.0387 | 45.2849 | 47.2757 | 59.5662 | 58.6022 | 30.768 | 39.5433 | 12.4585 | 22.1375 | 25.5099 | 13.4982
177 | 9.4811 | 12.2351 | 10.3796 | 7.774 | 6.7771 | 4.3365 | 5.1704 | 2.043 | 3.6065 | 6.2024 | 9.1224 | 17.652 | 22.169 | 17.4537 | 23.8437 | 56.4083 | 16.5768 | 11.9219 | 59.0204 | 31.2156 | 10.3432 | 26.1269 | 33.0099 | 24.2534
178 | 23.3311 | 8.1894 | 13.9126 | 10.8707 | 12.9233 | 15.7277 | 14.927 | 4.5202 | 2.8749 | 0 | 0 | 2.5586 | 5.9219 | 6.6597 | 2.8113 | 1.5836 | 13.0681 | 11.7074 | 21.0548 | 58.8573 | 59.6 | 59.6 | 1.2567 | 0
179 | 59.6 | 59.0449 | 54.4015 | 54.2764 | 58.1984 | 57.9792 | 54.6555 | 32.749 | 15.6045 | 19.7378 | 13.1137 | 0 | 2.5154 | 51.4276 | 50.6787 | 0.93794 | 5.2409 | 24.5788 | 16.6801 | 5.0302 | 0.43284 | 31.4652 | 25.2918 | 19.5696
180 | 24.9475 | 20.8015 | 15.3778 | 22.8275 | 30.4436 | 31.6064 | 25.6574 | 12.6887 | 0.29212 | 0 | 0 | 0 | 0 | 0 | 0.080086 | 0.21006 | 0 | 3.7898 | 16.0557 | 54.9077 | 48.9392 | 58.6423 | 57.1312 | 52.1005
181 | 29.7548 | 52.2095 | 20.4819 | 10.0356 | 25.1455 | 41.6553 | 17.4546 | 36.4087 | 11.1017 | 0 | 0 | 0.88011 | 0.12013 | 1.4469 | 1.5483 | 2.645 | 5.527 | 39.9571 | 56.3269 | 53.0841 | 59.6 | 47.6592 | 4.1932 | 13.054
182 | 25.0822 | 35.2687 | 15.7965 | 11.8822 | 20.0689 | 23.0549 | 5.7774 | 13.1021 | 11.0859 | 0 | 0 | 0.72716 | 1.4956 | 2.1025 | 3.2658 | 6.6489 | 6.9827 | 21.1345 | 34.8 | 59.6 | 34.644 | 53.7989 | 59.6 | 59.5575
183 | 19.7073 | 19.3749 | 19.1893 | 1.0169 | 0.12013 | 0 | 6.1364 | 2.9692 | 2.8077 | 0 | 0 | 0 | 15.0347 | 57.3328 | 24.0396 | 48.1646 | 11.7344 | 39.9176 | 50.27 | 42.0409 | 42.2585 | 43.9869 | 58.1064 | 58.5045
184 | 27.5509 | 17.3119 | 40.5021 | 11.2312 | 15.8936 | 59.3137 | 51.9242 | 53.9061 | 46.492 | 35.8658 | 29.6468 | 9.6889 | 10.3941 | 59.5717 | 39.9065 | 0 | 58.1517 | 0.12108 | 18.0339 | 0.040043 | 6.7964 | 0.52563 | 2.2028 | 1.6584
185 | 2.7586 | 14.5472 | 17.1366 | 5.573 | 14.0795 | 31.705 | 25.8179 | 24.7502 | 5.6925 | 0.16023 | 0 | 3.285 | 8.8601 | 7.1954 | 6.1769 | 8.4145 | 20.45 | 26.9603 | 16.5979 | 36.2062 | 56.9989 | 53.2128 | 42.8691 | 38.3733
186 | 42.7756 | 36.0236 | 32.1257 | 12.377 | 16.3991 | 41.9248 | 25.3621 | 17.1473 | 2.9774 | 0.93555 | 0 | 0 | 0.21579 | 8.5488 | 8.7294 | 8.2461 | 11.4385 | 20.8677 | 19.206 | 7.6968 | 54.2768 | 59.6 | 30.9182 | 36.4104
187 | 18.8109 | 59.4135 | 11.4814 | 17.4636 | 12.6333 | 9.0869 | 0.77437 | 0 | 0 | 0 | 0 | 0.49508 | 2.4478 | 56.2529 | 59.6 | 59.6 | 30.7265 | 59.5651 | 25.3897 | 47.5023 | 27.3542 | 2.2508 | 0.46572 | 3.3291
188 | 0.17999 | 0.69148 | 1.6999 | 0.41087 | 1.2629 | 0.20129 | 1.236 | 1.0868 | 0 | 0 | 1.8625 | 4.4022 | 3.05 | 2.3511 | 40.3943 | 54.702 | 13.3824 | 50.8522 | 32.7734 | 17.4346 | 53.4364 | 45.4257 | 2.5884 | 0.64176
189 | 10.8415 | 1.0205 | 0 | 3.6386 | 0.70729 | 6.5979 | 17.7682 | 3.0941 | 0.81137 | 4.2762 | 17.9147 | 23.2824 | 32.8611 | 23.2876 | 27.117 | 39.6267 | 43.2345 | 31.0639 | 14.2894 | 10.094 | 50.6126 | 59.6 | 59.6 | 59.6
190 | 59.6 | 59.6 | 59.6 | 32.5318 | 43.7001 | 30.3734 | 31.3944 | 19.4493 | 5.3198 | 13.2142 | 14.4623 | 16.6411 | 21.3 | 14.5144 | 5.975 | 9.5 | 8.1428 | 5.3404 | 0.71218 | 4.1284 | 18.1065 | 51.2393 | 36.8862 | 40.6794
191 | 42.2936 | 31.0488 | 23.6599 | 31.8939 | 53.6354 | 40.5548 | 22.4399 | 17.5479 | 3.6812 | 0 | 0 | 15.1857 | 17.5848 | 54.8595 | 57.9369 | 27.0528 | 23.7366 | 34.1548 | 21.8827 | 3.6047 | 59.6 | 14.8488 | 5.8797 | 7.1441
192 | 2.2941 | 2.0956 | 7.5199 | 28.2548 | 36.1988 | 25.989 | 19.3374 | 26.713 | 9.5002 | 56.699 | 28.9562 | 51.0803 | 59.6 | 59.6 | 25.9752 | 50.9655 | 57.9378 | 58.3472 | 47.4295 | 55.0599 | 50.6975 | 58.6945 | 57.1909 | 25.3813
193 | 38.7987 | 17.9537 | 4.3201 | 2.5246 | 6.4279 | 17.1409 | 15.3685 | 6.5109 | 1.0708 | 0.16644 | 0 | 0 | 0 | 0 | 59.6 | 52.0027 | 59.6 | 59.6 | 10.8663 | 8.0743 | 0 | 0 | 6.1754 | 41.462
194 | 54.684 | 41.4461 | 56.8123 | 56.9325 | 55.2554 | 54.5819 | 44.1049 | 19.1244 | 5.2462 | 0.9115 | 0 | 0 | 0 | 0 | 59.569 | 11.3461 | 59.6 | 35.4687 | 33.5511 | 50.8303 | 53.9461 | 56.0551 | 57.5256 | 44.4866
195 | 16.2926 | 6.4233 | 2.3263 | 0 | 3.923 | 13.1949 | 16.1445 | 15.9764 | 19.3408 | 13.7506 | 3.3562 | 0 | 0 | 0 | 57.7245 | 57.9278 | 28.1896 | 9.4547 | 21.8514 | 11.9826 | 35.4408 | 30.5915 | 11.5965 | 9.6576
196 | 15.7358 | 18.9324 | 46.0013 | 46.6423 | 15.5816 | 13.7463 | 7.0133 | 27.228 | 10.6262 | 10.4833 | 5.4756 | 3.0984 | 0 | 0.2852 | 52.8793 | 20.4614 | 55.0032 | 50.7771 | 4.2004 | 26.4961 | 5.5484 | 37.4113 | 14.6718 | 6.1555
197 | 6.655 | 14.587 | 2.8141 | 0 | 0 | 0.16023 | 0 | 0.81447 | 0.22719 | 1.5083 | 4.2383 | 7.9285 | 9.3667 | 6.8316 | 10.681 | 14.2058 | 20.6755 | 44.8462 | 56.4747 | 53.3404 | 53.3751 | 59.6 | 58.6374 | 57.1019
198 | 56.3593 | 44.849 | 30.8995 | 23.5684 | 13.12 | 10.6074 | 5.65 | 0.92589 | 0.12013 | 0.080086 | 0 | 1.6004 | 48.8085 | 46.7442 | 5.6609 | 15.6019 | 17.3911 | 35.2593 | 2.1944 | 9.5815 | 22.6033 | 0 | 0 | 0.39554
199 | 4.5921 | 6.435 | 17.6278 | 23.5381 | 18.8692 | 11.9219 | 7.6674 | 2.5301 | 0.040043 | 0.25583 | 0 | 0 | 2.1936 | 20.8899 | 49.4295 | 8.4923 | 57.6898 | 44.2109 | 38.6754 | 59.4456 | 51.3687 | 59.6 | 59.6 | 11.8603
200 | 9.1473 | 21.2261 | 2.3797 | 0.15999 | 4.3161 | 19.3469 | 20.0405 | 17.9969 | 4.3632 | 1.195 | 0 | 0 | 0 | 0 | 27.6005 | 59.0936 | 1.184 | 46.1785 | 4.9355 | 9.4146 | 5.0052 | 0.69553 | 21.9822 | 49.9755
201 | 31.422 | 37.0095 | 14.0457 | 9.8459 | 9.2475 | 5.5213 | 11.0806 | 9.558 | 1.1291 | 5.3173 | 3.5054 | 5.7482 | 9.2294 | 10.9565 | 11.4962 | 28.0098 | 51.4229 | 59.0914 | 57.7491 | 54.7641 | 59.6 | 59.1859 | 51.5745 | 30.8679
202 | 45.1286 | 32.1598 | 7.3879 | 4.4506 | 36.5008 | 46.837 | 7.2635 | 0 | 5.5918 | 18.1373 | 14.2796 | 6.3734 | 4.9258 | 14.7695 | 10.7888 | 10.9519 | 20.7126 | 16.2353 | 20.3631 | 11.8047 | 56.1765 | 59.5116 | 19.7532 | 23.5701
203 | 17.3346 | 17.0984 | 6.1545 | 4.4731 | 0 | 0 | 0 | 0 | 0 | 0.74101 | 3.5398 | 25.9578 | 33.2054 | 32.1428 | 50.6568 | 45.3497 | 20.7329 | 0.82074 | 48.6118 | 1.4363 | 0 | 0.13368 | 0 | 0.12013
204 | 2.6428 | 1.0708 | 0.21036 | 0 | 0.92929 | 2.5268 | 7.3157 | 7.6666 | 4.5576 | 3.7275 | 5.2921 | 18.9831 | 20.5248 | 19.169 | 42.2653 | 20.4199 | 59.6 | 59.6 | 57.7813 | 54.5552 | 59.6 | 59.4609 | 53.7053 | 34.2174
205 | 7.4054 | 0.98216 | 3.788 | 14.8395 | 12.4358 | 11.1368 | 10.7399 | 2.4968 | 0.25058 | 0 | 0 | 3.6123 | 8.5447 | 11.3235 | 25.2753 | 17.1414 | 4.5532 | 34.7662 | 45.3561 | 46.8246 | 56.2386 | 11.9616 | 29.8284 | 21.106
206 | 20.3558 | 2.649 | 1.281 | 1.5148 | 4.1292 | 8.1157 | 21.645 | 9.5737 | 1.9268 | 3.2296 | 4.0563 | 1.0871 | 0 | 0 | 59.6 | 7.9236 | 36.3582 | 2.6939 | 4.8861 | 0.7943 | 0 | 13.9416 | 44.1525 | 37.3498
207 | 43.047 | 19.2651 | 15.0738 | 15.5239 | 11.4928 | 10.44 | 16.0643 | 23.8294 | 21.6028 | 20.8052 | 21.7752 | 29.5556 | 29.0393 | 18.2975 | 15.6575 | 4.7901 | 7.3951 | 11.9618 | 2.4749 | 0 | 3.2478 | 0.226 | 0.48141 | 3.2345
208 | 14.4035 | 14.0354 | 12.7016 | 19.6899 | 23.7026 | 17.5959 | 12.3923 | 6.8532 | 5.1785 | 5.6121 | 6.0552 | 6.0865 | 6.7884 | 4.9364 | 3.6102 | 5.6974 | 3.3538 | 6.9745 | 12.852 | 7.1025 | 8.1178 | 6.6642 | 3.5763 | 0.62141
209 | 0 | 0 | 2.4676 | 3.646 | 7.8078 | 7.1591 | 4.7235 | 3.4924 | 0.16023 | 0 | 0 | 1.2095 | 4.9437 | 5.8261 | 5.546 | 6.5309 | 13.1057 | 23.3411 | 12.3383 | 6.5505 | 0.169 | 0.50123 | 0.2852 | 5.2034
210 | 20.3868 | 31.7954 | 24.4781 | 27.3418 | 19.7777 | 24.5683 | 16.4653 | 2.0754 | 1.2045 | 13.0172 | 23.6842 | 16.7506 | 8.9934 | 10.5627 | 13.8082 | 12.7991 | 10.7792 | 12.7782 | 48.0369 | 3.1422 | 0.60679 | 20.1489 | 14.5933 | 37.749
211 | 28.6082 | 19.9842 | 13.842 | 12.0579 | 10.6511 | 7.4974 | 3.2512 | 0.3996 | 1.449 | 1.7472 | 6.7934 | 11.4843 | 12.3525 | 14.6118 | 19.2732 | 16.0294 | 26.0067 | 20.2985 | 30.0288 | 14.2195 | 21.072 | 11.5442 | 17.1786 | 12.7508
212 | 22.9321 | 40.8425 | 59.0123 | 28.0866 | 24.3785 | 1.0511 | 1.3797 | 0 | 1.5807 | 14.7365 | 11.6979 | 4.4093 | 4.8002 | 4.2264 | 7.9936 | 15.3522 | 22.4451 | 10.1208 | 1.8557 | 57.2448 | 56.6594 | 57.681 | 58.386 | 57.9869
213 | 0 | 37.8753 | 58.5192 | 58.6941 | 58.4279 | 58.8299 | 59.0697 | 34.2725 | 20.8036 | 17.8387 | 3.7566 | 2.1476 | 0.50248 | 1.249 | 6.3598 | 5.8083 | 58.8425 | 8.4191 | 52.8134 | 56.5381 | 5.7782 | 36.3424 | 16.0134 | 3.3466
214 | 4.2406 | 15.0431 | 20.3565 | 37.5388 | 39.1536 | 15.5903 | 9.3792 | 10.7586 | 3.2095 | 3.2942 | 7.3882 | 13.8169 | 21.0043 | 25.5564 | 59.6 | 48.336 | 0.77013 | 12.3227 | 43.913 | 36.791 | 28.199 | 5.5354 | 6.4343 | 9.1331
215 | 4.498 | 7.4237 | 5.074 | 0.35717 | 6.4625 | 5.685 | 7.1663 | 7.5916 | 2.2009 | 1.103 | 0.90888 | 1.4744 | 1.1453 | 0.39918 | 4.5295 | 40.9832 | 11.8441 | 0.12013 | 7.8545 | 4.1258 | 52.6108 | 59.4848 | 8.3734 | 48.4108
216 | 58.8035 | 59.4565 | 58.0602 | 59.5348 | 53.8004 | 44.3472 | 26.5197 | 14.3983 | 15.2829 | 21.1323 | 20.4609 | 20.6577 | 10.7042 | 16.5828 | 14.615 | 16.4531 | 28.7635 | 52.9367 | 23.2477 | 24.2595 | 6.0238 | 5.225 | 5.0613 | 9.698
217 | 14.0939 | 12.9103 | 11.8448 | 10.793 | 9.6273 | 7.4406 | 4.2052 | 0.20028 | 0.36045 | 2.0156 | 4.7987 | 10.6009 | 14.9329 | 16.2731 | 15.9513 | 21.6161 | 37.6327 | 17.3719 | 54.7654 | 38.2634 | 36.3577 | 49.2327 | 30.5631 | 36.9102
218 | 43.766 | 28.8699 | 31.8588 | 26.5531 | 35.5643 | 21.2408 | 9.9724 | 14.1575 | 24.1061 | 27.0151 | 25.5785 | 15.0259 | 8.2266 | 2.5395 | 0.47879 | 7.4601 | 11.8213 | 28.9345 | 59.6 | 2.8212 | 53.3817 | 16.5873 | 54.4883 | 17.5354
219 | 8.6731 | 16.6381 | 3.4934 | 13.6055 | 54.3471 | 55.4972 | 52.1955 | 33.9121 | 19.1882 | 8.7804 | 0 | 0.769 | 7.4617 | 12.0214 | 14.9905 | 48.2781 | 25.4268 | 58.6231 | 59.6 | 59.3 | 23.0546 | 40.0869 | 44.9101 | 35.6858
220 | 2.651 | 2.3742 | 5.3956 | 8.32 | 31.7579 | 52.81 | 56.5441 | 54.7499 | 33.2429 | 35.373 | 22.2609 | 9.1374 | 0.49347 | 0 | 0 | 0 | 0 | 0 | 0 | 0.086591 | 8.963 | 45.9115 | 23.8284 | 21.8011
221 | 58.3303 | 54.6658 | 57.9158 | 57.4521 | 54.178 | 50.9209 | 45.93 | 28.1046 | 12.8413 | 5.8224 | 5.5825 | 8.6254 | 5.292 | 2.9294 | 0.90028 | 0.30214 | 0 | 0.040043 | 0.80832 | 1.1745 | 0.16262 | 35.3334 | 59.6 | 21.0345
222 | 46.3593 | 49.6191 | 55.7707 | 23.3518 | 12.2726 | 17.4328 | 24.6107 | 14.8237 | 5.7395 | 4.0717 | 2.0448 | 0.71922 | 7.7145 | 14.4004 | 7.0958 | 59.6 | 32.1139 | 58.2122 | 38.7783 | 54.4431 | 0.51059 | 2.4705 | 2.4037 | 4.3032
223 | 7.694 | 6.2978 | 9.5821 | 4.8897 | 2.7998 | 7.1122 | 2.3416 | 2.5281 | 0.16023 | 0 | 0 | 0 | 0.79985 | 1.5068 | 2.4236 | 4.276 | 5.7155 | 9.575 | 14.3172 | 15.8401 | 24.5994 | 11.4547 | 34.3411 | 24.0298
224 | 14.4415 | 4.2624 | 0.33127 | 2.0104 | 9.5349 | 13.9173 | 13.2451 | 2.1941 | 7.0963 | 19.1379 | 17.282 | 12.7624 | 11.0292 | 14.208 | 6.9275 | 6.5184 | 15.1283 | 14.4568 | 26.4492 | 21.1991 | 14.7285 | 2.1306 | 2.9337 | 4.6605
225 | 1.0947 | 3.7655 | 2.3488 | 1.8257 | 3.5858 | 4.8532 | 12.1663 | 18.6096 | 25.1958 | 56.3122 | 58.629 | 52.4207 | 15.5614 | 3.0234 | 28.3794 | 55.7406 | 18.3237 | 1.6492 | 59.6 | 57.158 | 6.062 | 4.09 | 8.2717 | 3.0105
226 | 17.3173 | 19.9918 | 19.5155 | 15.5589 | 10.8831 | 5.1023 | 3.1789 | 0.42466 | 0 | 0 | 0 | 0.88948 | 4.6698 | 1.151 | 57.7044 | 31.8572 | 18.0099 | 13.2635 | 5.4752 | 13.7409 | 11.5057 | 3.9281 | 1.9847 | 7.3108
227 | 41.6628 | 34.4991 | 24.462 | 4.8832 | 16.3312 | 15.3504 | 16.2677 | 13.1715 | 3.5612 | 1.6209 | 1.962 | 3.8145 | 5.222 | 4.3145 | 3.6096 | 2.3193 | 3.2241 | 25.2569 | 0.12013 | 25.4944 | 7.7455 | 54.9415 | 59.5628 | 59.6
228 | 10.7684 | 17.3133 | 30.1296 | 6.9845 | 8.05 | 13.6605 | 10.8804 | 21.1345 | 5.6438 | 2.229 | 0 | 2.6824 | 10.2731 | 13.5722 | 17.2523 | 23.122 | 44.2091 | 57.3961 | 59.6 | 59.6 | 54.4549 | 40.3765 | 22.9888 | 14.9607
229 | 11.2771 | 16.7577 | 20.7544 | 30.939 | 59.004 | 59.0304 | 59.3983 | 52.5318 | 29.4359 | 18.5911 | 9.5672 | 6.5683 | 3.3969 | 1.5059 | 0.6787 | 0.080086 | 1.2457 | 2.9974 | 3.3109 | 9.613 | 10.7809 | 12.3534 | 12.5608 | 14.1552
230 | 33.2372 | 16.9005 | 33.9557 | 28.1072 | 49.515 | 21.3713 | 1.8648 | 3.4794 | 6.4785 | 6.9683 | 4.4573 | 0.69428 | 6.0522 | 6.7786 | 8.7092 | 16.5704 | 15.2854 | 30.9907 | 36.393 | 44.45 | 44.485 | 12.1025 | 0.040043 | 6.7137
231 | 14.5261 | 17.6066 | 20.5501 | 5.9622 | 0.21185 | 2.5486 | 3.7792 | 7.7828 | 0 | 0 | 0.14913 | 2.8579 | 4.5262 | 26.2581 | 51.3709 | 59.351 | 59.6 | 15.3257 | 58.7319 | 38.5029 | 59.6 | 59.6 | 26.8626 | 12.2997
232 | 32.1002 | 59.4847 | 59.6 | 58.0772 | 59.4647 | 46.728 | 32.9608 | 22.0258 | 10.7054 | 32.3346 | 45.1129 | 47.1399 | 36.8978 | 16.6139 | 1.6414 | 0 | 22.3787 | 33.1718 | 18.4321 | 3.1272 | 5.341 | 6.0333 | 51.693 | 57.089
233 | 39.9636 | 33.9367 | 36.0409 | 26.825 | 21.64 | 15.264 | 12.3631 | 4.9313 | 1.3912 | 0.52868 | 1.9784 | 0 | 0.82205 | 2.3791 | 7.776 | 6.7911 | 18.1342 | 7.6021 | 40.9144 | 51.3872 | 20.061 | 8.3473 | 28.7401 | 14.5955
234 | 27.1053 | 5.6226 | 3.4704 | 3.0724 | 3.3734 | 2.7623 | 0.51692 | 0 | 0 | 0 | 0.7977 | 2.1707 | 19.4296 | 5.2501 | 4.0437 | 12.2093 | 13.1211 | 35.9969 | 26.3654 | 43.267 | 36.1232 | 1.7812 | 3.6097 | 0.040043
235 | 0.38754 | 3.1559 | 3.8228 | 0.49192 | 0.73313 | 2.8853 | 0.61199 | 1.2094 | 3.6587 | 4.5533 | 9.2105 | 20.7989 | 22.6351 | 26.3791 | 21.0631 | 48.6467 | 19.3442 | 6.175 | 5.9351 | 3.8809 | 25.7058 | 46.6634 | 35.1927 | 25.3933
236 | 44.5299 | 58.5788 | 55.7491 | 50.0941 | 46.5514 | 40.4641 | 34.2073 | 22.8986 | 13.8068 | 19.5354 | 24.5976 | 30.4192 | 28.774 | 34.0791 | 22.3632 | 12.5728 | 13.9307 | 8.765 | 2.1827 | 39.4573 | 42.858 | 33.1466 | 42.9035 | 49.8097
237 | 25.8519 | 6.3333 | 11.4582 | 13.6165 | 11.2117 | 5.7567 | 3.6116 | 0.20499 | 2.9296 | 6.6652 | 4.0604 | 3.0589 | 4.0222 | 1.7007 | 18.2294 | 7.9568 | 7.1317 | 39.9643 | 26.086 | 12.8802 | 5.6776 | 2.8933 | 59.6 | 0.251
238 | 10.1798 | 23.0603 | 20.2988 | 4.6192 | 0 | 0.040043 | 8.5782 | 9.0739 | 7.6938 | 13.9711 | 0.71529 | 5.9502 | 6.3572 | 14.8867 | 9.5091 | 7.7424 | 1.6965 | 4.4839 | 44.1453 | 32.5161 | 9.9405 | 12.003 | 9.595 | 5.6053
239 | 5.6718 | 5.7887 | 4.7456 | 2.6557 | 0.50904 | 0.12842 | 0 | 0 | 0 | 0 | 0.13529 | 4.4568 | 5.255 | 8.0573 | 13.1707 | 17.1849 | 17.5696 | 16.8234 | 19.7953 | 33.6528 | 37.1288 | 42.4995 | 22.1118 | 16.6997
240 | 11.1174 | 6.4234 | 2.1404 | 2.6832 | 3.4293 | 9.2456 | 13.4793 | 6.1258 | 0.52975 | 0.040043 | 0 | 0 | 1.4648 | 7.4683 | 7.5069 | 9.2414 | 8.821 | 13.9752 | 18.5667 | 29.6886 | 29.9759 | 16.1925 | 7.4565 | 0.80462
241 | 0.69201 | 0.72847 | 1.7038 | 2.1109 | 2.3384 | 8.789 | 8.1975 | 4.29 | 0.040043 | 0 | 0.29319 | 7.0061 | 15.1028 | 20.191 | 26.9185 | 28.6101 | 36.5419 | 55.0887 | 59.6 | 44.7227 | 46.3561 | 59.6 | 28.2924 | 51.3503
242 | 45.4967 | 44.8409 | 29.2589 | 6.6843 | 2.7712 | 0.2593 | 0 | 0 | 0 | 0 | 0.27678 | 10.2194 | 24.9543 | 35.5612 | 55.7995 | 47.597 | 43.5804 | 33.6112 | 15.0664 | 10.1807 | 8.0597 | 4.3059 | 0 | 3.202
243 | 4.4807 | 2.4578 | 2.7881 | 3.2786 | 6.7777 | 11.9093 | 12.9554 | 15.2513 | 11.863 | 19.8479 | 12.1131 | 1.9566 | 1.5524 | 1.364 | 0.88465 | 0.64397 | 1.0923 | 8.7089 | 15.2159 | 21.7915 | 25.0492 | 0.25482 | 23.1877 | 35.2127
244 | 8.1854 | 8.8845 | 7.4871 | 4.9412 | 2.4598 | 0.80122 | 0 | 0.16023 | 0 | 0.61312 | 1.9753 | 4.8162 | 6.6912 | 9.4126 | 12.266 | 15.9742 | 18.698 | 24.2286 | 24.4008 | 44.117 | 48.4763 | 41.4839 | 16.0719 | 6.0013
245 | 9.9676 | 16.7298 | 8.9824 | 7.7641 | 5.2011 | 2.2442 | 0.57254 | 0.728 | 1.5835 | 0 | 2.6144 | 6.1745 | 12.3719 | 16.1496 | 11.3219 | 10.9685 | 41.7349 | 21.9035 | 13.6206 | 32.3813 | 39.3183 | 4.6827 | 0.17121 | 12.4649
246 | 48.4124 | 12.4663 | 36.6144 | 34.5045 | 37.5069 | 16.1057 | 11.5467 | 6.1892 | 5.7546 | 0 | 0 | 6.868 | 19.33 | 14.6743 | 22.3057 | 27.3327 | 41.0151 | 59.1053 | 59.6 | 58.1797 | 52.5652 | 52.4057 | 35.0266 | 43.3907
247 | 26.2673 | 23.43 | 28.4488 | 24.924 | 23.7182 | 20.0963 | 21.9567 | 21.4598 | 8.649 | 4.0117 | 2.1533 | 3.2693 | 6.7909 | 8.0541 | 4.483 | 7.3075 | 11.5596 | 22.415 | 43.8851 | 48.3555 | 58.5576 | 59.6 | 57.5379 | 39.125
248 | 13.6569 | 8.6837 | 16.4808 | 17.0596 | 46.5191 | 42.0122 | 45.372 | 53.3636 | 24.281 | 30.2138 | 16.9603 | 1.9216 | 0 | 0 | 0 | 0 | 52.7575 | 18.0888 | 0 | 7.7499 | 59.6 | 54.9915 | 52.3462 | 38.1867
249 | 37.7379 | 58.6445 | 59.033 | 58.8603 | 54.8314 | 52.2028 | 55.346 | 41.0015 | 22.9781 | 15.7871 | 1.1822 | 0 | 0 | 0 | 26.8016 | 34.8732 | 5.9321 | 5.0718 | 6.2079 | 4.5206 | 0.040043 | 0.16841 | 4.0559 | 28.9395
250 | 5.9741 | 14.4934 | 19.1466 | 47.7473 | 49.0037 | 50.6096 | 55.3776 | 51.4217 | 34.6617 | 28.6821 | 13.2136 | 4.3658 | 4.778 | 3.4963 | 59.6 | 51.4879 | 32.8809 | 14.6129 | 5.9364 | 0.31384 | 0 | 0 | 0 | 0.84467
251 | 2.7382 | 0.84031 | 0.35364 | 0 | 0 | 0.90363 | 6.4709 | 0.45629 | 0.20028 | 0.080086 | 0 | 0 | 4.9479 | 9.8901 | 3.3547 | 59.6 | 22.4177 | 33.194 | 31.4884 | 4.19 | 0.49753 | 0 | 5.2689 | 8.5795
252 | 0.33497 | 24.7356 | 59.6 | 59.6 | 59.6 | 59.6 | 56.6476 | 45.2101 | 15.4229 | 11.4343 | 6.647 | 6.6049 | 7.3588 | 0.66223 | 0 | 0 | 37.3528 | 21.1888 | 0 | 23.7946 | 28.6957 | 6.4717 | 0 | 9.768
253 | 26.4739 | 33.8951 | 41.0603 | 46.8317 | 59.6 | 57.2621 | 48.9141 | 51.4671 | 36.131 | 16.1294 | 2.9734 | 7.0443 | 4.8102 | 50.1507 | 6.602 | 13.6632 | 0.20028 | 1.9492 | 5.6467 | 3.5428 | 10.741 | 41.4275 | 6.5652 | 1.1533
254 | 15.1516 | 19.5451 | 8.8719 | 10.8531 | 1.5372 | 2.4358 | 2.3238 | 2.2825 | 1.5993 | 3.9828 | 9.2241 | 13.1695 | 13.5209 | 1.7766 | 47.3913 | 33.5067 | 17.9968 | 22.5294 | 38.5927 | 59.6 | 50.2914 | 12.5821 | 19.3881 | 15.1173
255 | 5.6802 | 3.6405 | 1.2905 | 0.81047 | 1.5311 | 0.77437 | 3.3688 | 7.9874 | 22.9544 | 27.553 | 23.3024 | 13.7204 | 12.5887 | 15.2604 | 4.8619 | 29.6972 | 50.4084 | 40.3773 | 27.7637 | 4.0878 | 10.5768 | 19.9408 | 32.1036 | 32.0797
256 | 35.7582 | 31.117 | 34.778 | 57.7164 | 59.6 | 59.6 | 59.6 | 59.6 | 57.6945 | 49.4334 | 45.8085 | 38.2587 | 22.7553 | 17.3574 | 10.7458 | 5.6984 | 13.7637 | 19.562 | 8.6179 | 34.8465 | 56.5187 | 55.3854 | 51.3688 | 55.0645
257 | 57.3551 | 55.9715 | 57.1833 | 52.7111 | 50.7609 | 38.7883 | 35.662 | 41.751 | 35.0111 | 32.8847 | 21.4557 | 7.2305 | 1.0531 | 0 | 4.7139 | 18.0035 | 59.6 | 57.7393 | 57.8782 | 56.3756 | 46.9389 | 59.6 | 59.6 | 59.5916
258 | 59.6 | 59.6 | 59.6 | 43.462 | 41.7121 | 14.2529 | 3.3825 | 0 | 0.80773 | 7.4162 | 7.1874 | 5.9621 | 14.5822 | 30.706 | 26.6099 | 52.1648 | 45.0577 | 45.3755 | 42.5154 | 42.5291 | 2.3192 | 16.5915 | 11.8889 | 27.0381
259 | 0.72764 | 0.21639 | 4.0204 | 0.69876 | 0.77168 | 1.2558 | 4.2638 | 5.7936 | 2.3454 | 4.1335 | 5.6537 | 20.1946 | 18.4645 | 7.846 | 3.344 | 7.2648 | 4.9949 | 10.0979 | 40.6376 | 57.7436 | 59.6 | 51.5878 | 34.9455 | 36.0793
260 | 43.9838 | 52.1881 | 59.6 | 59.6 | 59.6 | 59.6 | 59.3984 | 55.6472 | 35.2756 | 17.2624 | 2.448 | 0 | 0 | 1.1845 | 0.24032 | 1.3686 | 5.3726 | 18.303 | 39.8826 | 50.7744 | 42.6709 | 35.367 | 22.864 | 24.8328
261 | 28.2095 | 33.1006 | 19.7787 | 8.669 | 10.5779 | 6.8487 | 6.5636 | 7.1656 | 10.3489 | 24.4978 | 25.8133 | 30.3737 | 40.6197 | 52.0316 | 47.9243 | 47.6424 | 50.4964 | 50.7125 | 44.9128 | 38.8323 | 21.7913 | 17.1081 | 14.5192 | 11.2373
262 | 9.4807 | 12.5703 | 12.2887 | 14.4275 | 14.9823 | 10.9219 | 7.0515 | 3.9782 | 2.1861 | 2.4954 | 2.1815 | 2.586 | 5.3679 | 11.0487 | 6.3844 | 4.9881 | 4.4721 | 5.9802 | 5.9361 | 3.6975 | 1.9683 | 11.0408 | 10.1995 | 4.6788
263 | 3.4161 | 9.49 | 10.7015 | 5.4774 | 5.4629 | 6.761 | 8.2038 | 9.7244 | 6.7117 | 0.59372 | 0 | 0 | 0.16023 | 0.080086 | 0.94486 | 6.1655 | 6.9219 | 10.9454 | 0.22242 | 2.5191 | 0.66235 | 0.040043 | 4.3145 | 13.7023
264 | 44.7596 | 59.3774 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 58.6124 | 58.2422 | 54.6658 | 37.3494 | 10.1667 | 2.1206 | 0.65668 | 0.76351 | 0.16023 | 0 | 1.3368 | 3.5425 | 29.1954 | 57.5486 | 55.6136 | 53.9336
265 | 44.8068 | 46.6681 | 59.5568 | 59.6 | 44.375 | 2.9655 | 3.9961 | 5.4337 | 0 | 0 | 0 | 0 | 0.33568 | 5.8823 | 6.2293 | 11.3714 | 18.6734 | 32.4875 | 22.3089 | 40.6616 | 58.2181 | 58.3218 | 59.6 | 59.3445
266 | 40.845 | 34.7059 | 36.0733 | 42.8599 | 59.0217 | 59.389 | 57.8556 | 58.7126 | 54.6384 | 33.3977 | 39.528 | 55.8253 | 57.2329 | 43.9626 | 24.9801 | 18.7854 | 16.8829 | 7.4516 | 26.8203 | 39.0643 | 59.0073 | 59.5682 | 59.6 | 59.6
267 | 59.5597 | 59.5053 | 59.2681 | 58.8802 | 54.8547 | 33.1905 | 13.7418 | 15.1795 | 14.2365 | 2.4843 | 0.35681 | 1.4175 | 1.9659 | 3.9218 | 5.5575 | 7.5343 | 10.5913 | 14.2414 | 19.7206 | 24.8514 | 13.8651 | 16.8324 | 11.1314 | 21.0793
268 | 25.7266 | 32.8012 | 48.4766 | 36.8557 | 15.163 | 20.8786 | 19.4659 | 12.3788 | 10.0367 | 7.4884 | 5.1961 | 11.604 | 12.276 | 13.7807 | 21.5057 | 14.936 | 0.58579 | 6.6474 | 16.6106 | 2.4176 | 0 | 0.92511 | 23.5262 | 17.6121
269 | 27.7315 | 51.2629 | 57.5691 | 59.3617 | 59.6 | 59.5085 | 57.3388 | 26.664 | 7.6423 | 30.4592 | 28.4908 | 8.3991 | 2.5324 | 0.88262 | 1.2956 | 2.3687 | 5.4554 | 8.008 | 18.0533 | 18.9802 | 9.6937 | 16.0621 | 33.9802 | 35.3134
270 | 27.3986 | 22.4256 | 15.9918 | 14.7858 | 12.9605 | 11.509 | 10.4605 | 9.3006 | 5.8041 | 6.9558 | 4.662 | 2.5324 | 1.1642 | 4.1829 | 9.2063 | 10.3112 | 12.7103 | 15.7395 | 35.4235 | 28.1541 | 14.1043 | 19.2255 | 11.6333 | 2.6632
271 | 0.54431 | 0.12013 | 1.3271 | 6.3205 | 7.2734 | 10.1239 | 6.6546 | 5.2719 | 1.6055 | 0.12377 | 0 | 0 | 1.1561 | 3.3208 | 7.2868 | 7.0727 | 12.6412 | 35.9134 | 35.1177 | 22.0649 | 5.4175 | 1.4283 | 1.517 | 0.2109
272 | 3.8505 | 6.1619 | 10.2712 | 9.2916 | 9.2156 | 17.3676 | 31.5415 | 13.5893 | 5.0683 | 0 | 0.080086 | 1.902 | 6.9537 | 11.6749 | 18.8698 | 32.4212 | 44.656 | 48.521 | 42.4333 | 44.4118 | 31.5444 | 20.2615 | 3.3484 | 0.39202
273 | 0.12013 | 0.19473 | 0 | 0 | 0 | 0 | 0.12013 | 0.80934 | 0.92672 | 6.9607 | 20.3821 | 18.6766 | 13.85 | 13.0366 | 13.8855 | 5.2834 | 9.4205 | 14.7416 | 12.5697 | 14.669 | 11.7185 | 8.8356 | 7.8526 | 13.023
274 | 13.639 | 16.5964 | 23.6688 | 20.786 | 16.1297 | 17.6403 | 21.8932 | 20.8791 | 15.5308 | 2.7306 | 0 | 0 | 1.7977 | 1.7077 | 0.99833 | 0.67847 | 0.56597 | 2.1044 | 5.2911 | 6.0321 | 3.924 | 0.76046 | 0 | 4.3332
275 | 11.3663 | 25.5411 | 33.6189 | 14.6962 | 11.364 | 15.4877 | 21.1211 | 21.6388 | 20.5719 | 5.991 | 0.35973 | 0 | 0.72734 | 2.5675 | 2.8361 | 2.5591 | 4.9456 | 5.4101 | 19.4477 | 44.8138 | 19.3645 | 6.3036 | 7.5083 | 16.0897
276 | 48.2134 | 26.7153 | 24.0916 | 4.5063 | 2.0241 | 4.0185 | 9.4194 | 11.617 | 8.1886 | 1.6828 | 0 | 0 | 2.0729 | 3.2949 | 0.14191 | 55.7718 | 11.5113 | 0.080086 | 35.5439 | 58.7003 | 53.4507 | 59.6 | 59.5912 | 52.7859
277 | 51.1559 | 55.9803 | 53.2168 | 57.5384 | 59.3292 | 58.6296 | 58.9506 | 57.1436 | 45.2192 | 27.3023 | 18.2165 | 14.7218 | 2.941 | 0 | 1.2477 | 0 | 30.9322 | 0.040043 | 10.238 | 3.7696 | 0 | 8.7092 | 53.9885 | 58.6041
278 | 58.3055 | 53.0707 | 37.1354 | 57.5488 | 38.1557 | 54.5713 | 39.0995 | 13.2869 | 7.2469 | 10.6348 | 3.718 | 4.4376 | 7.2741 | 9.8497 | 12.2457 | 20.0128 | 18.8277 | 20.2159 | 28.3649 | 30.8885 | 21.242 | 12.9696 | 0.80611 | 1.4065
279 | 2.1229 | 0.080086 | 1.7686 | 0.50678 | 0.080086 | 0.16083 | 0.45617 | 0.055977 | 1.7727 | 3.495 | 9.689 | 18.5775 | 49.6151 | 35.0224 | 50.3375 | 16.7879 | 52.3587 | 41.225 | 31.2952 | 15.4082 | 32.86 | 43.4133 | 51.7387 | 59.0111
280 | 59.6 | 59.6 | 56.3762 | 24.1551 | 53.0172 | 59.0509 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 58.9058 | 53.5289 | 55.4221 | 37.4046 | 18.8422 | 6.9568 | 3.7966 | 6.0238 | 2.207 | 0 | 0
281 | 7.982 | 19.556 | 14.065 | 12.6195 | 15.5057 | 16.7462 | 11.1449 | 6.1026 | 5.5162 | 1.2064 | 2.5453 | 3.2196 | 4.0759 | 5.8518 | 9.1332 | 12.4051 | 12.2567 | 13.0195 | 18.0331 | 14.6572 | 10.0349 | 0.46279 | 0.080086 | 10.267
282 | 20.3419 | 26.9124 | 24.7851 | 15.0784 | 6.8968 | 11.1254 | 3.5082 | 0.46196 | 0 | 1.3059 | 2.3535 | 0.67894 | 0.61592 | 0.47425 | 35.6994 | 43.6296 | 14.3371 | 5.8307 | 20.349 | 4.0205 | 7.9152 | 24.0402 | 58.3814 | 58.7832
283 | 59.6 | 59.5618 | 58.483 | 57.9809 | 58.7257 | 56.9712 | 49.4594 | 41.2111 | 28.6606 | 8.2788 | 2.177 | 0.38193 | 0.67703 | 0 | 4.4669 | 16.4519 | 8.9664 | 30.2549 | 20.3524 | 8.6827 | 33.3075 | 58.8037 | 59.6 | 46.6085
284 | 52.1441 | 43.2329 | 23.2052 | 46.9964 | 55.4003 | 58.4219 | 59.2935 | 58.7907 | 54.2255 | 50.4771 | 55.9375 | 59.6 | 59.6 | 59.6 | 57.2592 | 49.988 | 54.6156 | 59.1307 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 55.0896
285 | 47.0232 | 36.9476 | 20.3065 | 3.8728 | 17.5437 | 9.2575 | 4.0088 | 1.2848 | 13.763 | 17.4109 | 10.4221 | 15.2814 | 7.0401 | 9.2455 | 6.0624 | 10.9898 | 10.3786 | 8.4029 | 8.1954 | 9.2081 | 9.0122 | 15.9966 | 19.3668 | 25.3026
286 | 34.1249 | 27.9551 | 19.3855 | 12.2849 | 12.6603 | 11.9084 | 24.4716 | 28.4982 | 8.4609 | 3.4155 | 0.60864 | 0 | 0 | 0 | 0.66587 | 8.7921 | 40.7806 | 39.2935 | 59.6 | 59.6 | 50.7061 | 25.6184 | 18.7404 | 44.1946
287 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 59.0596 | 40.719 | 11.1497 | 3.9824 | 11.9437 | 8.8367 | 11.0017 | 7.9276 | 10.7427 | 13.6733 | 16.3392 | 23.6147 | 15.7894 | 15.8923 | 10.1931 | 6.2286 | 1.178
288 | 46.1696 | 47.9473 | 43.4938 | 26.3002 | 24.6974 | 34.9722 | 22.986 | 15.7626 | 7.6337 | 2.1693 | 4.0484 | 3.4764 | 2.677 | 5.4108 | 11.1449 | 13.586 | 13.7062 | 13.9419 | 11.4353 | 9.8023 | 28.4323 | 46.3994 | 1.8397 | 0
289 | 0.27702 | 0.27797 | 1.4649 | 0.52557 | 0.39154 | 0.28126 | 0.081578 | 0.16023 | 0.46315 | 0.40879 | 0.6398 | 2.676 | 5.7671 | 7.16 | 6.1931 | 7.4542 | 8.5745 | 10.7559 | 15.8947 | 11.4279 | 3.0453 | 5.4036 | 12.0317 | 15.4729
290 | 19.5537 | 26.272 | 20.8997 | 24.9696 | 37.4792 | 44.4151 | 38.2425 | 30.3328 | 27.3052 | 16.4586 | 8.7056 | 1.6945 | 0 | 0 | 0 | 0 | 0 | 1.693 | 3.0096 | 4.3539 | 3.1992 | 10.4755 | 48.6166 | 59.6
291 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 57.309 | 35.4666 | 19.2602 | 7.8745 | 0 | 0 | 0 | 0.26091 | 5.8387 | 3.1685 | 0.67357 | 0.84986 | 1.7065 | 6.2234 | 8.6994 | 24.4942
292 | 19.8967 | 25.1488 | 33.1794 | 13.2747 | 17.01 | 7.6428 | 4.8237 | 6.3903 | 7.8367 | 6.2534 | 10.1432 | 13.0776 | 8.4757 | 7.5392 | 11.8135 | 16.4982 | 17.6616 | 18.6001 | 23.521 | 20.0169 | 9.4952 | 11.0155 | 14.3548 | 7.8649
293 | 3.5935 | 6.9538 | 5.4316 | 0.69112 | 1.0388 | 0.27678 | 0.080086 | 0 | 0.040043 | 0.22594 | 1.2807 | 0.46995 | 3.3164 | 10.8071 | 24.2728 | 43.1131 | 17.9711 | 17.671 | 11.4411 | 16.7636 | 15.4746 | 13.6111 | 7.8296 | 10.1912
294 | 13.4409 | 11.863 | 5.3115 | 2.4724 | 2.8315 | 3.1229 | 2.6081 | 0.68998 | 1.5888 | 3.9508 | 5.3084 | 11.4957 | 8.3295 | 4.2471 | 5.6864 | 10.4634 | 12.6148 | 21.972 | 23.3441 | 12.7201 | 1.2555 | 7.6796 | 3.4719 | 5.9551
295 | 58.8797 | 59.5857 | 59.6 | 57.2703 | 39.3712 | 59.4894 | 59.5842 | 57.298 | 44.8036 | 26.7291 | 15.0881 | 15.9702 | 21.2126 | 17.9759 | 19.8218 | 20.8511 | 9.2292 | 0.97959 | 0.28329 | 0.83667 | 2.2247 | 0.68974 | 0.45539 | 10.8526
296 | 9.9063 | 5.4019 | 5.0311 | 12.2554 | 20.8885 | 30.2434 | 35.8998 | 42.3696 | 37.7691 | 21.9005 | 13.5382 | 5.6319 | 0.93663 | 0 | 0 | 0 | 0 | 0 | 9.6157 | 4.495 | 0.12496 | 18.3235 | 53.9909 | 56.7043
297 | 44.9605 | 50.6699 | 58.6872 | 59.6 | 59.6 | 59.5991 | 59.5621 | 57.6529 | 43.5412 | 32.1583 | 15.1078 | 8.7396 | 5.1046 | 1.2841 | 0 | 0 | 0 | 0.28036 | 0 | 0 | 0 | 0.86132 | 5.133 | 35.3479
298 | 51.2525 | 48.1242 | 39.5747 | 40.6422 | 59.1842 | 59.6 | 57.3377 | 47.2784 | 36.2333 | 15.7112 | 0.3358 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.8806 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6
299 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 59.1484 | 59.3879 | 59.6 | 59.0216 | 56.9792 | 57.9553 | 59.2326 | 19.1799 | 4.3264 | 48.2464 | 59.2721 | 55.8191 | 55.289 | 47.824 | 47.6221 | 51.3828
300 | 49.2942 | 55.0754 | 51.968 | 25.983 | 38.4819 | 59.6 | 55.8278 | 21.0511 | 0.74459 | 3.0425 | 2.428 | 2.9322 | 6.0923 | 10.6185 | 19.3045 | 41.0727 | 59.6 | 59.6 | 38.6646 | 12.0943 | 4.0379 | 0.4767 | 0 | 0.12013
301 | 3.7446 | 11.4499 | 14.3256 | 13.4145 | 8.0643 | 6.0869 | 7.5254 | 6.8613 | 8.4284 | 4.7863 | 6.6347 | 5.6644 | 5.0896 | 8.2436 | 6.8829 | 5.8577 | 6.3291 | 13.039 | 18.1382 | 12.4299 | 2.4863 | 0.51406 | 0.34093 | 0.39989
302 | 1.4839 | 10.5901 | 21.2156 | 43.9061 | 52.9119 | 56.0619 | 56.1228 | 57.3054 | 53.3048 | 41.5658 | 21.6416 | 12.3629 | 11.6209 | 16.6955 | 25.6129 | 33.8857 | 39.0838 | 59.0054 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 59.5894
303 | 45.6686 | 29.6329 | 15.8172 | 8.2401 | 8.5438 | 17.6394 | 30.766 | 22.7114 | 10.9004 | 0.12622 | 0 | 0 | 0 | 0.58095 | 3.2502 | 11.0326 | 16.824 | 15.6048 | 28.7855 | 28.7344 | 21.4515 | 28.5657 | 40.8781 | 33.2863
304 | 29.4516 | 27.5398 | 22.3245 | 18.9381 | 23.7419 | 19.3461 | 10.6062 | 3.73 | 0.080086 | 0 | 0.054962 | 0.087128 | 0.32661 | 18.6524 | 51.0313 | 59.6 | 59.6 | 59.6 | 59.6 | 59.0602 | 38.7284 | 59.6 | 57.9546 | 51.2075
305 | 59.6 | 59.6 | 55.3184 | 59.6 | 59.6 | 59.6 | 59.6 | 59.5843 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 56.0537 | 46.6244 | 44.398
306 | 24.1001 | 32.4388 | 29.8062 | 9.947 | 16.0437 | 16.0307 | 8.7026 | 4.6731 | 5.0098 | 2.0362 | 2.1049 | 3.2991 | 4.7716 | 6.2755 | 4.4705 | 2.2218 | 0.080086 | 0 | 0.19246 | 1.3015 | 1.2481 | 0.32088 | 1.726 | 15.2628
307 | 18.9083 | 18.4713 | 18.0978 | 20.2586 | 23.2936 | 26.1315 | 20.0337 | 20.4376 | 21.3432 | 21.0808 | 7.8398 | 2.3638 | 0.7237 | 0.51149 | 0.14257 | 0.23763 | 0.44608 | 0.84329 | 0.16023 | 0 | 0.19377 | 2.071 | 8.7914 | 9.1975
308 | 16.7951 | 42.2014 | 51.7087 | 54.6748 | 51.5528 | 29.204 | 11.7396 | 4.5047 | 0.22176 | 0 | 0 | 0.53429 | 6.2658 | 15.1158 | 24.3255 | 30.9371 | 29.5573 | 32.3059 | 43.0677 | 39.1738 | 26.8478 | 11.5701 | 15.7117 | 33.8208
309 | 59.5061 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 56.3109 | 49.0601 | 48.9663 | 53.0384 | 51.0909 | 48.9107 | 55.4028 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6
310 | 59.4544 | 59.5593 | 58.5967 | 57.7112 | 58.3643 | 57.6668 | 54.7155 | 54.8621 | 45.4682 | 29.3426 | 19.4842 | 20.6185 | 26.0577 | 25.706 | 20.2602 | 23.5522 | 38.0821 | 58.861 | 59.6 | 59.6 | 59.0763 | 59.6 | 59.3863 | 41.8479
311 | 16.1929 | 6.208 | 16.6076 | 9.3971 | 10.5379 | 7.2565 | 2.8674 | 1.6226 | 0.14167 | 0.080086 | 0.080086 | 0 | 1.03 | 7.1737 | 12.2561 | 19.3322 | 24.3395 | 45.5001 | 32.8514 | 59.3509 | 59.2415 | 59.6 | 55.6137 | 43.3651
312 | 59.4623 | 44.5323 | 19.9414 | 12.8256 | 11.7236 | 7.9762 | 2.4892 | 6.1049 | 12.5266 | 9.7582 | 4.487 | 3.2612 | 4.7001 | 5.0487 | 4.8552 | 4.5268 | 1.2721 | 1.8216 | 0 | 0 | 0 | 1.203 | 5.3315 | 13.1458
313 | 26.1026 | 20.9827 | 15.4411 | 20.0978 | 31.491 | 37.2277 | 30.705 | 36.0199 | 37.9271 | 28.0146 | 12.5478 | 12.0745 | 9.5543 | 5.2905 | 0.56884 | 0 | 0.32106 | 4.638 | 4.7011 | 1.3791 | 0.080086 | 0 | 0.080086 | 6.3314
314 | 23.2528 | 32.6811 | 30.0648 | 23.737 | 16.4862 | 7.6482 | 3.2488 | 3.5726 | 4.7787 | 5.0205 | 1.1886 | 0.27941 | 1.333 | 0.75032 | 0.092141 | 1.0044 | 10.1812 | 19.0317 | 18.8397 | 6.9837 | 3.2439 | 1.3383 | 0.98688 | 1.397
315 | 4.3849 | 16.355 | 13.6582 | 10.2577 | 19.4205 | 33.4808 | 39.1019 | 55.1013 | 58.7945 | 52.0316 | 30.4472 | 15.5397 | 7.4712 | 17.9746 | 14.0109 | 5.9216 | 0.226 | 4.6912 | 0 | 0 | 26.5497 | 26.9934 | 40.8586 | 58.7361
316 | 59.4272 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 59.4718 | 59.1259 | 57.1787 | 49.1769 | 21.098 | 12.3647 | 6.572 | 0.83947 | 0 | 5.3425 | 9.5828 | 3.1182 | 0.12013 | 0 | 2.0341 | 28.4285 | 59.0763 | 59.6
317 | 59.4277 | 48.054 | 21.7069 | 15.7819 | 14.9715 | 21.9821 | 26.1782 | 30.325 | 29.1847 | 28.1941 | 15.3315 | 13.8254 | 15.7822 | 20.5303 | 13.5007 | 13.9634 | 29.1032 | 59.1879 | 59.6 | 52.3487 | 56.7642 | 59.6 | 59.6 | 59.6
318 | 59.6 | 59.6 | 59.483 | 54.5464 | 23.6181 | 4.6794 | 20.8817 | 14.2076 | 15.715 | 10.3032 | 16.236 | 14.3845 | 16.9391 | 26.3817 | 29.7162 | 38.0934 | 34.2075 | 22.3187 | 16.6523 | 19.2855 | 13.6411 | 5.9808 | 4.064 | 3.8498
319 | 21.7957 | 20.1154 | 21.2389 | 15.4127 | 9.454 | 8.125 | 6.9418 | 4.9075 | 7.7529 | 11.2502 | 10.765 | 13.4347 | 11.9092 | 18.0728 | 23.7733 | 43.2175 | 45.902 | 32.6217 | 34.2659 | 19.7111 | 24.592 | 21.6195 | 15.8194 | 12.5901
320 | 7.9007 | 4.8717 | 3.6413 | 3.8984 | 3.7984 | 1.3229 | 0.17563 | 0.08307 | 0 | 3.1947 | 11.3652 | 16.6249 | 19.1664 | 14.5286 | 41.0616 | 43.6171 | 26.8998 | 28.9042 | 19.5844 | 39.2354 | 33.4084 | 23.012 | 17.3445 | 15.9546
321 | 13.6333 | 11.6534 | 9.4988 | 9.2833 | 7.8825 | 10.7645 | 8.0054 | 6.2111 | 6.4993 | 3.891 | 4.0649 | 3.6427 | 3.4819 | 2.1808 | 1.4302 | 0.95095 | 0 | 0 | 0 | 0.86883 | 2.0798 | 0.90279 | 4.7935 | 21.3956
322 | 28.6656 | 35.0717 | 45.055 | 46.9115 | 33.6613 | 19.6985 | 11.074 | 11.807 | 10.4866 | 7.9652 | 1.6663 | 3.219 | 3.9183 | 3.705 | 2.0824 | 2.129 | 1.5543 | 1.8855 | 0.65483 | 0.59325 | 1.3003 | 3.6969 | 6.4259 | 5.3765
323 | 3.3902 | 3.9152 | 3.5416 | 8.4992 | 21.3274 | 32.7763 | 33.3276 | 28.9909 | 24.7541 | 14.541 | 2.2666 | 0.1733 | 0.42102 | 1.6667 | 1.0395 | 0.16035 | 0.42048 | 1.2842 | 0.32828 | 0 | 0.89259 | 0.59635 | 1.3961 | 3.0827
324 | 6.7153 | 17.9818 | 14.3061 | 10.9965 | 12.9797 | 21.5043 | 38.5959 | 36.3997 | 39.028 | 27.7559 | 17.4019 | 8.0891 | 3.6284 | 1.3566 | 0.093096 | 0 | 0 | 0.29409 | 7.4962 | 26.8638 | 40.8468 | 35.4943 | 22.2272 | 15.7976
325 | 11.1335 | 11.0755 | 14.7583 | 14.1353 | 10.7766 | 5.9532 | 4.8793 | 21.9497 | 39.5018 | 56.9087 | 43.3625 | 32.1585 | 44.9161 | 58.7376 | 57.1986 | 57.005 | 57.3843 | 49.1108 | 21.7516 | 27.0366 | 51.9924 | 59.6 | 59.6 | 59.6
326 | 59.6 | 59.6 | 59.5363 | 59.2553 | 59.4375 | 59.3081 | 58.0395 | 58.0361 | 56.7207 | 45.0118 | 32.0537 | 22.3746 | 19.4737 | 15.2219 | 12.1651 | 17.8289 | 34.4191 | 53.1044 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6
327 | 59.6 | 59.6 | 59.6 | 58.6173 | 54.4321 | 40.0662 | 28.5268 | 25.0974 | 25.9589 | 34.7567 | 4.7379 | 0.080086 | 0.92159 | 0.4511 | 0.040043 | 0.29928 | 1.8828 | 2.5302 | 1.0443 | 1.4121 | 14.7721 | 25.6276 | 40.7148 | 52.8698
328 | 58.8626 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 59.5822 | 43.9565 | 59.6 | 59.6 | 59.6 | 59.6 | 59.0453 | 27.2632 | 12.8429 | 6.6278 | 4.4335 | 13.9629 | 59.6 | 59.6
329 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 57.9652 | 58.8338 | 32.3411 | 28.5152 | 13.2873 | 8.3946 | 3.8389 | 5.353 | 8.053 | 0.28925 | 0.3204 | 3.5016 | 57.5472 | 47.5267 | 12.0057 | 12.9185
330 | 27.2357 | 50.2327 | 59.6 | 59.1662 | 59.1203 | 59.6 | 59.2153 | 57.1441 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 55.3343 | 30.8934 | 17.2713 | 4.5384 | 0.88453 | 0.83929 | 0.40544 | 0 | 0 | 0 | 0
331 | 3.2011 | 8.2809 | 17.1792 | 38.1918 | 55.0961 | 57.8813 | 54.0325 | 54.3972 | 55.7311 | 48.3885 | 20.7421 | 8.8304 | 8.6838 | 3.8548 | 0.12013 | 0 | 0 | 12.0566 | 50.5414 | 58.8557 | 59.6 | 59.6 | 59.6 | 59.6
332 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 59.5188 | 58.7364 | 52.6509 | 29.5551 | 10.5488 | 10.4695 | 10.0731 | 3.9496 | 11.022 | 49.7393 | 59.2471 | 27.6762 | 14.5613 | 16.5507 | 10.9625 | 7.2052 | 6.5395
333 | 4.5119 | 1.9469 | 1.3172 | 0.78535 | 0.097989 | 0.36361 | 0.41893 | 1.9775 | 4.3202 | 6.1665 | 0.75843 | 0.61771 | 0.24211 | 0.19902 | 0.13403 | 0.21722 | 1.2966 | 2.0542 | 3.5319 | 8.8027 | 9.3613 | 16.5572 | 6.1311 | 27.9598
334 | 44.407 | 56.6333 | 58.0787 | 59.3701 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 59.329 | 40.8607 | 51.1512 | 59.6 | 59.6 | 59.6 | 59.4769 | 59.5524 | 59.6 | 59.6 | 59.6 | 59.1149 | 25.0051 | 18.8041 | 4.9539
335 | 17.9581 | 13.2329 | 14.1262 | 18.9683 | 28.2454 | 34.6003 | 54.2415 | 56.787 | 50.4822 | 44.9641 | 38.9727 | 39.082 | 33.5535 | 23.776 | 11.9429 | 2.093 | 2.387 | 10.6696 | 32.0325 | 52.5893 | 59.6 | 59.6 | 59.6 | 59.6
336 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 58.8789 | 55.0725 | 22.0349 | 5.4847 | 2.7068 | 1.4331 | 0.13827 | 1.5502 | 5.8474 | 8.2887 | 48.5622 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6
337 | 59.6 | 59.6 | 59.6 | 58.9408 | 49.281 | 27.0821 | 3.6358 | 8.9626 | 22.9182 | 23.4433 | 18.1083 | 13.6429 | 11.9635 | 12.0107 | 11.6539 | 11.105 | 9.3402 | 7.0021 | 2.1521 | 1.7236 | 2.6613 | 7.2374 | 11.8286 | 19.298
338 | 18.7064 | 31.6799 | 43.8114 | 54.2928 | 56.3074 | 52.3928 | 52.8442 | 53.1066 | 32.4878 | 20.4413 | 31.0192 | 57.4294 | 48.673 | 53.8737 | 54.3046 | 58.7435 | 59.6 | 59.6 | 58.4178 | 57.2077 | 58.5285 | 55.8889 | 56.4694 | 59.1456
339 | 59.3905 | 59.4491 | 53.6533 | 43.8586 | 36.0839 | 28.3131 | 14.1163 | 4.4488 | 3.7365 | 11.6856 | 7.5492 | 4.579 | 0 | 8.466 | 31.3527 | 45.1621 | 37.7902 | 30.129 | 19.2032 | 17.3926 | 21.1336 | 19.924 | 32.9788 | 59.0046
340 | 59.6 | 57.7486 | 18.6115 | 27.3307 | 31.5759 | 41.5333 | 51.3582 | 26.994 | 23.0815 | 15.4747 | 9.6966 | 7.7905 | 11.7104 | 12.7965 | 17.4745 | 32.173 | 21.0795 | 30.8004 | 29.1012 | 18.2698 | 16.8524 | 16.9709 | 18.3458 | 19.1584
341 | 15.9166 | 13.5885 | 11.1528 | 12.9957 | 15.1439 | 10.1428 | 9.5095 | 6.8939 | 4.6184 | 3.4059 | 0.50624 | 0.080086 | 0.040043 | 0 | 0 | 0.22045 | 0 | 0 | 2.552 | 4.2936 | 14.0667 | 14.578 | 30.6344 | 59.1351
342 | 59.6 | 59.6 | 57.1341 | 54.4888 | 53.2367 | 47.6827 | 42.6998 | 39.3788 | 33.5214 | 21.0632 | 7.4854 | 2.5277 | 2.0007 | 3.9067 | 3.1249 | 3.465 | 8.5115 | 12.4757 | 8.4903 | 7.0474 | 4.8286 | 0 | 0 | 1.5694
343 | 6.7598 | 11.5107 | 14.9724 | 29.942 | 38.0918 | 43.5836 | 46.0551 | 50.4697 | 49.4032 | 38.8451 | 35.114 | 32.7785 | 39.8085 | 41.5419 | 42.4856 | 43.1651 | 39.7278 | 49.758 | 39.9119 | 27.383 | 25.3994 | 18.3966 | 16.1148 | 14.9934
344 | 16.326 | 17.5562 | 15.4899 | 16.5051 | 14.6177 | 12.2922 | 10.3742 | 7.7339 | 5.954 | 1.522 | 0.43361 | 0.17539 | 0 | 0 | 0 | 0.41428 | 3.6042 | 8.2714 | 10.8779 | 7.6712 | 11.9893 | 10.3468 | 5.5152 | 12.7895
345 | 22.7483 | 30.6574 | 37.431 | 43.3581 | 47.7687 | 47.3919 | 38.1468 | 34.1218 | 35.2464 | 29.1716 | 14.4718 | 3.299 | 0.47568 | 0.84944 | 2.2655 | 1.4763 | 0.3315 | 0 | 0 | 0.27642 | 1.4618 | 2.6193 | 7.6159 | 14.5527
346 | 18.1851 | 24.324 | 17.1545 | 28.9767 | 55.9283 | 56.3634 | 57.163 | 58.2799 | 59.2285 | 59.0191 | 37.1059 | 13.4725 | 8.3273 | 3.1108 | 1.3959 | 0.64493 | 1.6014 | 0.48971 | 0.19747 | 0.20923 | 1.4373 | 2.3918 | 2.1073 | 0.78845
347 | 1.0781 | 6.4275 | 13.3854 | 23.1172 | 35.2563 | 40.3724 | 43.1149 | 38.4036 | 45.5802 | 47.7653 | 31.3902 | 10.7416 | 1.4405 | 0.040043 | 0 | 0.50123 | 3.5311 | 10.7628 | 11.2293 | 4.5458 | 7.3503 | 36.3968 | 55.7211 | 52.8215
348 | 51.6837 | 54.9757 | 51.9167 | 57.9685 | 59.4232 | 58.7914 | 54.6052 | 43.5173 | 43.6573 | 48.2054 | 32.9062 | 16.4281 | 9.1237 | 7.5633 | 7.9062 | 9.0254 | 15.7864 | 27.5554 | 50.132 | 31.2761 | 28.9615 | 26.2416 | 19.0908 | 20.1753
349 | 9.634 | 6.1203 | 7.3129 | 13.5102 | 17.7291 | 18.8701 | 14.5827 | 9.918 | 9.0337 | 7.6065 | 2.2852 | 4.0988 | 7.3175 | 8.7394 | 9.4945 | 13.914 | 23.6101 | 49.7812 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6
350 | 58.9468 | 56.9473 | 53.2321 | 48.0591 | 30.455 | 14.1419 | 6.7692 | 2.4513 | 2.2738 | 2.5353 | 1.2998 | 0 | 0 | 1.002 | 5.1037 | 9.8511 | 11.9386 | 19.5234 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 59.0272
351 | 55.5475 | 49.4795 | 37.4387 | 35.0287 | 32.0583 | 28.295 | 20.9103 | 20.5236 | 26.7642 | 30.758 | 16.4879 | 16.7201 | 23.316 | 26.2543 | 22.2903 | 18.9511 | 12.5853 | 35.9792 | 24.855 | 38.3001 | 19.629 | 4.1674 | 0.23035 | 0.080086
352 | 0 | 0.080086 | 0.084801 | 1.486 | 4.4576 | 16.2095 | 27.166 | 14.8852 | 16.8841 | 29.801 | 32.4826 | 42.6625 | 52.6659 | 49.4512 | 49.9726 | 49.5328 | 57.2533 | 53.5374 | 58.0088 | 59.327 | 59.6 | 59.5746 | 59.6 | 59.6
353 | 59.6 | 59.6 | 59.4657 | 59.3051 | 58.7862 | 53.3381 | 33.3572 | 17.9711 | 15.1429 | 11.7799 | 1.1245 | 0.83577 | 4.0613 | 3.2508 | 5.6656 | 10.2082 | 10.9253 | 14.2188 | 7.3385 | 2.2521 | 3.8832 | 6.0958 | 10.0184 | 7.7078
354 | 7.3352 | 21.2835 | 50.084 | 59.5632 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 53.8827 | 22.6354 | 5.2575 | 6.7519 | 5.0819 | 0.26156 | 0 | 0 | 0.56962 | 0.80808 | 7.3059 | 12.3212 | 1.7011 | 8.9046 | 52.71
355 | 55.9235 | 58.2223 | 59.5227 | 59.6 | 59.0827 | 53.2301 | 31.082 | 25.9361 | 28.6273 | 34.7916 | 22.1316 | 1.4071 | 0 | 0.080086 | 0 | 0.64922 | 3.4938 | 13.7315 | 43.9619 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6
356 | 8.7015 | 14.8198 | 11.2894 | 7.3293 | 4.2443 | 2.0242 | 1.3445 | 1.3055 | 2.5831 | 2.6692 | 4.2757 | 8.2959 | 16.1644 | 23.3466 | 27.6413 | 31.1494 | 25.9958 | 28.9172 | 22.3471 | 19.4116 | 13.102 | 6.3781 | 5.1699 | 3.0057
357 | 1.3094 | 0.080086 | 2.8272 | 3.838 | 2.056 | 2.8357 | 13.7849 | 17.1518 | 11.0221 | 16.1632 | 20.1415 | 27.0064 | 27.7316 | 31.6094 | 14.7442 | 3.252 | 0 | 0 | 0 | 0.84663 | 3.2054 | 11.7551 | 52.97 | 59.399
358 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 59.2871 | 48.288 | 40.0267 | 33.582 | 29.8136 | 29.2024 | 31.3138 | 32.4112 | 40.1174 | 52.7621 | 53.6472 | 53.3614 | 40.6498 | 24.1845 | 13.3897
359 | 13.2711 | 10.8269 | 6.5346 | 4.4814 | 5.469 | 5.8586 | 3.9908 | 2.7447 | 0.94301 | 0.26711 | 7.276 | 10.8844 | 11.143 | 9.5745 | 9.7754 | 13.9946 | 18.2268 | 19.7319 | 14.6177 | 12.8012 | 12.3777 | 12.4252 | 18.4801 | 16.271
360 | 15.118 | 12.877 | 16.8651 | 31.5419 | 37.4842 | 51.1528 | 57.602 | 58.3935 | 57.7168 | 49.3121 | 33.6183 | 26.9801 | 9.9851 | 6.0942 | 4.4585 | 2.8365 | 0.38659 | 0 | 0 | 1.7452 | 15.7145 | 46.4071 | 58.1529 | 56.5846
361 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 58.1441 | 56.4231 | 48.4845 | 36.5904 | 22.4699 | 10.5565 | 9.5788 | 24.8305 | 59.2488 | 59.6 | 59.6 | 59.6 | 59.6
362 | 54.99 | 24.556 | 4.4452 | 5.9734 | 12.8868 | 15.9702 | 26.0648 | 38.6592 | 50.6753 | 48.8978 | 23.773 | 6.3348 | 6.372 | 7.6916 | 4.0453 | 5.786 | 10.8 | 9.023 | 13.775 | 6.4896 | 4.44 | 3.6844 | 6.8401 | 20.4338
363 | 26.277 | 22.2589 | 18.2325 | 17.9869 | 22.4311 | 25.6305 | 24.1585 | 19.6401 | 20.922 | 23.2617 | 19.0631 | 18.9382 | 21.4512 | 26.8311 | 31.3921 | 29.9111 | 27.883 | 18.3262 | 20.6763 | 22.233 | 23.4659 | 17.8358 | 19.0983 | 7.566
364 | 3.8574 | 4.1174 | 3.1422 | 0.34756 | 1.848 | 1.7454 | 1.5941 | 13.7612 | 34.0727 | 32.8522 | 51.3141 | 56.9575 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 53.3336 | 59.6 | 59.6 | 59.6 | 58.6268 | 58.1014 | 57.9566
365 | 57.6228 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 59.6 | 59.4736 | 59.4017 | 59.0294 | 59.6 | 59.6 | 59.548 | 57.3015 | 59.6 | 59.6 | 59.5536 | 59.3169 | 59.2279 | 59.3174 | 59.4962
TMY - Energy Profile
version 1-1b
CLIENT: BLACK HILLS CORP.
PROJECT: LA CUMBRE
TURBINE: GE2.5-127 and GE2.3-116
HUB HEIGHT: 80M and 89M
ALL DATA PRESENTED IN THIS PRELIMINARY REPORT ARE DRAFT AND ARE SUBJECT TO CHANGE DURING THE FINAL QUALITY CONTROL PROCESS.

## 12x24
Date are in local time (UTC -7)
Values represent the average value for each hour of the each month based on the 37-year timeseries
MWh | HOUR
Month | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | Total
1 | 32.4 | 33.1 | 33.4 | 33.9 | 34.2 | 33.9 | 33.1 | 32.7 | 32.8 | 31.8 | 27.8 | 24.8 | 23.4 | 22.4 | 22 | 23.5 | 24.6 | 27.2 | 28.2 | 27.5 | 26.3 | 26.6 | 28.7 | 30.6 | 21541.9
2 | 28.4 | 29 | 30.9 | 32 | 32.4 | 31.4 | 31.3 | 31.3 | 30.9 | 29.5 | 25.5 | 24.9 | 24.2 | 22.9 | 23.6 | 25.6 | 26.3 | 25 | 26.2 | 26 | 24.6 | 24.3 | 26.1 | 28.2 | 20475.5
3 | 24.2 | 24.2 | 26.2 | 26.7 | 28.4 | 28.5 | 27.7 | 27.4 | 27.1 | 24.2 | 22.1 | 22.1 | 21.5 | 22.7 | 24.7 | 25.9 | 25.8 | 26.6 | 26.1 | 26 | 25.1 | 24.9 | 24.9 | 23.5 | 17588.5
4 | 23.5 | 24.8 | 27.7 | 29.2 | 26.8 | 27 | 27.2 | 26.4 | 24.4 | 23.1 | 22.7 | 23.1 | 22 | 22.3 | 24.5 | 27.2 | 27.7 | 28.6 | 28.4 | 30 | 28.9 | 28.2 | 27.1 | 24.5 | 19384.3
5 | 22.2 | 21.7 | 23.5 | 24.8 | 23.6 | 23.2 | 22.5 | 19.5 | 17.4 | 17.1 | 18.4 | 19.1 | 19.9 | 22.6 | 25.3 | 27.3 | 29.6 | 31.4 | 32.5 | 30.6 | 28.9 | 28.1 | 25.9 | 24.8 | 17397
6 | 26.1 | 25.1 | 25.7 | 25.4 | 24.9 | 23.4 | 20.4 | 14.8 | 11 | 10.8 | 11.3 | 12.7 | 13.7 | 17 | 22.4 | 23.3 | 24.6 | 28.6 | 30.1 | 28.9 | 29.6 | 30.3 | 26.5 | 26.1 | 16513.7
7 | 26.1 | 23.5 | 22 | 22.8 | 23.6 | 24.5 | 23.3 | 17.6 | 10.3 | 9.8 | 9.1 | 8.9 | 8.5 | 9.5 | 13.5 | 17.9 | 19.7 | 23.8 | 27.1 | 27.2 | 26.3 | 27.3 | 26.4 | 26.4 | 14253
8 | 23.5 | 22.7 | 22.7 | 22.1 | 22 | 21.7 | 21.5 | 18.7 | 12.6 | 11.3 | 10.1 | 9.5 | 9.6 | 11.5 | 12.7 | 15.6 | 17.6 | 19.1 | 20.8 | 24.9 | 24.5 | 25 | 24.3 | 22.9 | 13853.9
9 | 25.5 | 25.9 | 26.9 | 26.3 | 25.8 | 24.2 | 24.3 | 23 | 18.5 | 14.1 | 12.2 | 11.9 | 13.2 | 14.5 | 15.5 | 17.3 | 19.6 | 20.9 | 24.5 | 27.6 | 26.9 | 27 | 26.8 | 26.9 | 16098.3
10 | 28.1 | 28.6 | 28.3 | 28.5 | 29 | 29 | 27 | 24.8 | 20.8 | 16.6 | 14.7 | 15.3 | 17 | 16.9 | 17.4 | 19.2 | 19.5 | 20.6 | 23.1 | 24 | 23.8 | 25.1 | 26.8 | 27.9 | 16560
11 | 30.5 | 31.4 | 31 | 31.5 | 31.6 | 30.7 | 29 | 29 | 28.5 | 26.1 | 21.8 | 19.8 | 20.7 | 21.6 | 21.6 | 22.7 | 22.4 | 24 | 24.8 | 26.3 | 27.7 | 28.6 | 29.3 | 30 | 19858.6
12 | 30.7 | 32 | 32.1 | 33.3 | 34.5 | 33.9 | 32.5 | 31.1 | 30.3 | 28.4 | 24.2 | 20.9 | 21.3 | 21.2 | 21.2 | 21.5 | 22.7 | 25 | 26.1 | 25.6 | 27.1 | 27.4 | 29.3 | 30.2 | 19875
[25 empty] | 213399.7 | MWh
12x24 - Energy Profile
version 1-1
ALL DATA PRESENTED IN THIS PRELIMINARY REPORT ARE DRAFT AND ARE SUBJECT TO CHANGE DURING THE FINAL QUALITY CONTROL PROCESS.
CLIENT: BLACK HILLS CORP.
PROJECT: LA CUMBRE
TURBINE: GE2.5-127 and GE2.3-116
HUB HEIGHT: 80M and 89M